## Outages
Details of outages
Summary of monthly EGF NCS – MWh & running hours
Month/Year | Service | Running MWh | Running Hours | Reason For Use
2018-10-01 | West Kalgoorlie NCS | 736.0 | 17.5 | Run: EGF planned outage (17 Oct)
2018-11-01 | West Kalgoorlie NCS
2018-12-01 | West Kalgoorlie NCS
2019-01-01 | West Kalgoorlie NCS
2019-02-01 | West Kalgoorlie NCS
2019-03-01 | West Kalgoorlie NCS | 817.0 | 19.0 | Run: planned (775.3 MWh) and unplanned outages (41.7 MWh)
2019-04-01 | West Kalgoorlie NCS | 95.5 |  | Run: EGF planned outage (1-2 May) **
2019-05-01 | West Kalgoorlie NCS | 835.0 | 23.0 | Run: EGF planned outage (1-2 May)
2019-06-01 | West Kalgoorlie NCS
2019-07-01 | West Kalgoorlie NCS
2019-08-01 | West Kalgoorlie NCS
2019-09-01 | West Kalgoorlie NCS
2019-10-01 | West Kalgoorlie NCS
2019-11-01 | West Kalgoorlie NCS | 567.7 | 15.0 | Run: COMBINED MAINTENANCE ON MRT-CGT-YLN-WKT X1 (20 Nov)
2019-12-01 | West Kalgoorlie NCS
2020-01-01 | West Kalgoorlie NCS
2020-02-01 | West Kalgoorlie NCS
2020-03-01 | West Kalgoorlie NCS | 30.6 | 2.0 | Run: Test on 14/3 - 17/3 at no cost to WP
18 months |  | 3114.2 | 78.5 | Average 4-5 hours per month
** Additional information – April 2019 planned outage - this refers to the same planned outage in May (1-2 May 2019). Part of the outage is accounted for in April 2019 and the remaining is in May 2019. This is because of the difference in a trading day vs an actual day. The last trading day in a month finishes at 7am on the first day of the following month.
Additional service details
eNAR# | eNAR Work | Date/time | Outage Description
351047 | MRT 220kV Bus A bay 1 modification works to install CB, CT and disconnector and combined maintenance. This is for the 220kV MRT bay 1 work for Merredin solar farm. | 17/10/2018, 0500 to 2200hrs | MRT-CGT-YLN-WKT X1 outage
366531 | Reinstate WKT 220kV busbar B and commissioning of new Variable Shunt Reactor (VSR), CB, CT and Disconnector (MRS work) | 27/03/2019, 0430 to 2100hrs | MRT-CGT-YLN-WKT X1 outage
369378 | MRT 220kV Bus A bay 1 commissioning of new CB, CT and disconnector (MRS work)
369014 | HV Testing, Maintenance, washing and sylgarding | 01/05/2019, 0700 to 1700hrs | MU-NGS-KDN X1 outage for major maintenance work
366625 | HV Testing, Maintenance, washing and sylgarding | 02/05/2019, 0700 to 2100hrs
383218 (MRT-KDN X1) and E#383033 (MRT-CGT-YLN-WKT X1) | HV Testing and Protection Maintenance | 19/11/2019, 0400 to 2000hrs | MRT-KDN X1 and
MRT-CGT-YLN-WKT X1 outage for major maintenance work
383224 (MRT-KDN X1) and E#383122 (MRT-CGT-YLN-WKT X1) | HV Testing and Protection Maintenance | 20/11/2019, 0530 to 2130hrs
406042, 406092 & 406093 | HV Testing, Protection Maintenance and repair work | 1. Tuesday 05/05/2020, 02:00 to 22:00 | MRT-KDN X1 and
|  | 2. Wednesday 06/05/2020, 02:00 to 22:00 | MRT-CGT-YLN-WKT X1 outage for major maintenance work
3. Thursday 07/05/2020, 02:00 to 22:00