## Appendix B1
FEEDER | SCNRRR_AREA | LOCAL_GOVERNMENT_AREA | CUSTOMERS | SAIDI | SAIDI_SSB | SAIFI | SAIFI_SSB
A 502.0 WYCHROSS ST | Urban | Total - City of Stirling | 3105 | 280.7 | 123.8 | 2.81 | 1.25
A 503.0 ARKANA RD EAST | Urban | Total - City of Stirling | 8310 | 87.4 | 123.8 | 0.47 | 1.25
A 505.0 CURLINGTON CRES | Urban | Total - City of Stirling | 1593 | 194.8 | 123.8 | 1.32 | 1.25
A 506.0 WADHURST ST | Rural Short | City of Wanneroo | 2966 | 153.4 | 202.5 | 3.08 | 2.09
A 506.0 WADHURST ST | Rural Short | City of Stirling | 1453 | 79.5 | 202.5 | 1.6 | 2.09
A 506.0 WADHURST ST | Rural Short | Total | 4419 | 129.3 | 202.5 | 2.6 | 2.09
A 510.0 WILMINGTON CR L/S | Urban | Total - City of Stirling | 1940 | 357.2 | 123.8 | 1.96 | 1.25
A 511.0 WALDERTON AVE | Urban | Total - City of Stirling | 2810 | 68.6 | 123.8 | 0.84 | 1.25
A 513.0 STORRINGTON CRES | Urban | Total - City of Stirling | 684 | 60.8 | 123.8 | 0.2 | 1.25
A 514.0 ARKANA WEST | Urban | Total - City of Stirling | 2314 | 327.2 | 123.8 | 3.39 | 1.25
ALB 504.0 TIMEWELL | Rural Short | Total - City of Albany | 2847 | 10 | 202.5 | 0.06 | 2.09
ALB 505.0 LANCASTER | Rural Short | Total - City of Albany | 4612 | 45.2 | 202.5 | 1.35 | 2.09
ALB 508.0 GLADVILLE | Rural Short | Total - City of Albany | 4589 | 69.5 | 202.5 | 1.97 | 2.09
ALB 512.0 ALBANY HIGHWAY SOUTH | Rural Short | Total - City of Albany | 5204 | 211.1 | 202.5 | 3.92 | 2.09
ALB 514.0 WILLYUNG | Rural Long | City of Albany | 1491 | 480.4 | 290.5 | 5.17 | 5.45
ALB 514.0 WILLYUNG | Rural Long | Shire of Jerramungup | 760 | 2986.8 | 290.5 | 32.17 | 5.45
ALB 514.0 WILLYUNG | Rural Long | Total | 2284 | 1326 | 290.5 | 14.28 | 5.45
ALB 517.0 CRANBROOK | Rural Short | Shire of Plantagenet | 40 | 291.8 | 202.5 | 3.07 | 2.09
ALB 517.0 CRANBROOK | Rural Short | City of Albany | 24 | 159.4 | 202.5 | 1.68 | 2.09
ALB 517.0 CRANBROOK | Rural Short | Total | 64 | 242.8 | 202.5 | 2.56 | 2.09
ALB 518.0 MT BARKER | Rural Short | City of Albany | 230 | 68.2 | 202.5 | 1.27 | 2.09
ALB 518.0 MT BARKER | Rural Short | Shire of Plantagenet | 26 | 243.2 | 202.5 | 4.53 | 2.09
ALB 518.0 MT BARKER | Rural Short | Total | 256 | 86 | 202.5 | 1.6 | 2.09
ALB 520.0 DENMARK | Rural Long | Shire of Denmark | 1797 | 418.9 | 290.5 | 4.17 | 5.45
ALB 520.0 DENMARK | Rural Long | Shire of Manjimup | 596 | 1038.6 | 290.5 | 10.34 | 5.45
ALB 520.0 DENMARK | Rural Long | City of Albany | 236 | 196.9 | 290.5 | 1.96 | 5.45
ALB 520.0 DENMARK | Rural Long | Total | 2628 | 539 | 290.5 | 5.36 | 5.45
ALB 530.0 LOWER DENMARK | Rural Long | Shire of Denmark | 2252 | 703.9 | 290.5 | 8.96 | 5.45
ALB 530.0 LOWER DENMARK | Rural Long | City of Albany | 1042 | 351.2 | 290.5 | 4.47 | 5.45
ALB 530.0 LOWER DENMARK | Rural Long | Total | 3294 | 591.5 | 290.5 | 7.53 | 5.45
AMT 503.0 36 WATKINS ST | Urban | City of Fremantle | 2471 | 34.8 | 123.8 | 0.7 | 1.25
AMT 503.0 36 WATKINS ST | Urban | City of Cockburn | 65 | 9.7 | 123.8 | 0.2 | 1.25
AMT 503.0 36 WATKINS ST | Urban | Total | 2536 | 34.2 | 123.8 | 0.69 | 1.25
AMT 504.0 L1819 BLINCO ST RMU | Urban | Total - City of Melville | 4262 | 70.1 | 123.8 | 0.17 | 1.25
AMT 506.0 2 ABSOLON ST RMU | Urban | Total - City of Melville | 3204 | 189.1 | 123.8 | 0.4 | 1.25
AMT 507.0 5 HALE ST | Urban | Total - City of Cockburn | 2127 | 270 | 123.8 | 3.58 | 1.25
AMT 512.0 LEFROY RD | Urban | City of Cockburn | 2661 | 156.4 | 123.8 | 1.9 | 1.25
AMT 512.0 LEFROY RD | Urban | City of Fremantle | 1351 | 355.1 | 123.8 | 4.32 | 1.25
AMT 512.0 LEFROY RD | Urban | Total | 4012 | 221.9 | 123.8 | 2.7 | 1.25
AMT 519.0 72 LEACH HWY | Rural Short | Total - City of Melville | 2195 | 0.6 | 202.5 | 0 | 2.09
AMT 520.0 STEVENS ST | Urban | City of Melville | 982 | 75.1 | 123.8 | 0.47 | 1.25
AMT 520.0 STEVENS ST | Urban | Town of East Fremantle | 884 | 146.2 | 123.8 | 0.92 | 1.25
AMT 520.0 STEVENS ST | Urban | City of Fremantle | 422 | 236.8 | 123.8 | 1.5 | 1.25
AMT 520.0 STEVENS ST | Urban | Total | 2289 | 132.4 | 123.8 | 0.84 | 1.25
AMT 523.0 L128 KNUSTSFORD ST | Urban | Town of East Fremantle | 2051 | 5 | 123.8 | 0.02 | 1.25
AMT 523.0 L128 KNUSTSFORD ST | Urban | City of Fremantle | 974 | 1.4 | 123.8 | 0.01 | 1.25
AMT 523.0 L128 KNUSTSFORD ST | Urban | Total | 3025 | 3.8 | 123.8 | 0.02 | 1.25
APM 503.0 L50 PHOENIX RD | Urban | Total - City of Cockburn | 1526 | 0 | 123.8 | 0 | 1.25
APM 504.0 179 NORTH LAKE RD 1 | Rural Short | Total - City of Cockburn | 2893 | 12.5 | 202.5 | 0.07 | 2.09
APM 511.0 L212 SUDLOW ST | Urban | City of Cockburn | 4433 | 107.8 | 123.8 | 1.72 | 1.25
APM 511.0 L212 SUDLOW ST | Urban | City of Fremantle | 627 | 95.7 | 123.8 | 1.53 | 1.25
APM 511.0 L212 SUDLOW ST | Urban | Total | 5060 | 106.2 | 123.8 | 1.69 | 1.25
APM 513.0 SPEARWOOD AVE | Urban | Total - City of Cockburn | 1173 | 273.2 | 123.8 | 1.79 | 1.25
BCH 501.0 BENARA RD WEST | Urban | City of Bayswater | 2487 | 286.8 | 123.8 | 1.32 | 1.25
BCH 501.0 BENARA RD WEST | Urban | City of Stirling | 825 | 368.3 | 123.8 | 1.7 | 1.25
BCH 501.0 BENARA RD WEST | Urban | Total | 3317 | 307.5 | 123.8 | 1.42 | 1.25
BCH 505.0 BENNETT SPRINGS DR | Rural Short | Total - City of Swan | 2654 | 301.8 | 202.5 | 3.43 | 2.09
BCH 506.0 WANDOO | Urban | City of Swan | 4050 | 48.5 | 123.8 | 0.13 | 1.25
BCH 506.0 WANDOO | Urban | City of Bayswater | 206 | 0 | 123.8 | 0 | 1.25
BCH 506.0 WANDOO | Urban | Total | 4256 | 46.1 | 123.8 | 0.13 | 1.25
BCH 508.0 WIDGEE RD WEST | Urban | City of Bayswater | 1286 | 123.3 | 123.8 | 3.6 | 1.25
BCH 508.0 WIDGEE RD WEST | Urban | City of Swan | 434 | 70.3 | 123.8 | 2.05 | 1.25
BCH 508.0 WIDGEE RD WEST | Urban | Total | 1723 | 110.1 | 123.8 | 3.21 | 1.25
BCH 509.0 BEECHBORO RD NORTH | Urban | Total - City of Swan | 2796 | 116.9 | 123.8 | 4.09 | 1.25
BCH 514.0 DELLA RD | Urban | Total - City of Swan | 543 | 59.7 | 123.8 | 6.46 | 1.25
BCH 516.0 BEECHBORO RD SOUTH | Urban | Total - City of Bayswater | 3370 | 83.8 | 123.8 | 0.39 | 1.25
BCH 518.0 122 BENARA RD | Rural Short | City of Swan | 5180 | 74.5 | 202.5 | 0.18 | 2.09
BCH 518.0 122 BENARA RD | Rural Short | City of Bayswater | 411 | 0 | 202.5 | 0 | 2.09
BCH 518.0 122 BENARA RD | Rural Short | Total | 5591 | 66.8 | 202.5 | 0.16 | 2.09
BCT 504.0 33 HENDON WAY RMU | Urban | City of Joondalup | 1385 | 181.3 | 123.8 | 1.25 | 1.25
BCT 504.0 33 HENDON WAY RMU | Urban | City of Stirling | 1180 | 218.9 | 123.8 | 1.52 | 1.25
BCT 504.0 33 HENDON WAY RMU | Urban | Total | 2565 | 198.6 | 123.8 | 1.37 | 1.25
BCT 505.0 BUNNINGS RMU | Urban | Total - City of Stirling | 647 | 16.5 | 123.8 | 0.01 | 1.25
BCT 536.0 163 BALCATTA RD RMU | Urban | Total - City of Stirling | 1726 | 111.7 | 123.8 | 1.37 | 1.25
BEL 502.0 BELGRAVIA ST | Urban | Total - City of Belmont | 861 | 17.6 | 123.8 | 0.02 | 1.25
BEL 504.0 DALY ST/BELMONT PUMP | Urban | Total - City of Belmont | 4063 | 206.4 | 123.8 | 4.03 | 1.25
BEL 505.0 BELMONT AVE | Urban | Total - City of Belmont | 940 | 14.1 | 123.8 | 0.1 | 1.25
BEL 508.0 FREDERICK ST | Urban | Total - City of Belmont | 1812 | 49.4 | 123.8 | 0.31 | 1.25
BEL 510.0 FISHER ST | Urban | Total - City of Belmont | 513 | 71.9 | 123.8 | 2.02 | 1.25
BEL 511.0 WRIGHT ST | Urban | Total - City of Belmont | 1434 | 47.3 | 123.8 | 0.24 | 1.25
BEL 514.0 GIBBS ST | Urban | Total - City of Belmont | 2095 | 240.1 | 123.8 | 1.35 | 1.25
BEL 517.0 AIRPORT NO1 | Urban | Total - City of Belmont | 1614 | 84.8 | 123.8 | 2.05 | 1.25
BIB 504.0 ROCKINGHAM RD | Urban | Total - City of Cockburn | 3249 | 173.6 | 123.8 | 2.38 | 1.25
BIB 505.0 L4 BUCKLEY ST RMU | Rural Short | Total - City of Cockburn | 2488 | 376.6 | 202.5 | 6.6 | 2.09
BIB 507.0 18 MIGUEL RD | Urban | Total - City of Cockburn | 3956 | 40.9 | 123.8 | 0.2 | 1.25
BIB 508.0 45 WELLARD RD | Urban | Total - City of Cockburn | 474 | 15.4 | 123.8 | 0.07 | 1.25
BIB 536.0 L101 MIGUEL RD | Urban | Total - City of Cockburn | 1644 | 19.8 | 123.8 | 0.15 | 1.25
BIB 537.0 OPP 5 PARKS ST | Rural Short | Total - City of Cockburn | 709 | 1.7 | 202.5 | 0 | 2.09
BIB 539.0 139 BARRINGTON ST | Urban | Total - City of Cockburn | 4724 | 660.4 | 123.8 | 4.83 | 1.25
BIB 540.0 L203 WENTWORTH PDE | Urban | Total - City of Cockburn | 2285 | 25.2 | 123.8 | 0.1 | 1.25
BKF 609.0 BROAD ARROW | Rural Short | City of Kalgoorlie-Boulder | 14 | 1291.9 | 202.5 | 2.44 | 2.09
BKF 609.0 BROAD ARROW | Rural Short | Shire of Menzies | 2 | 4752.8 | 202.5 | 8.99 | 2.09
BKF 609.0 BROAD ARROW | Rural Short | Total | 16 | 1651.5 | 202.5 | 3.13 | 2.09
BKF 611.0 ORA BANDA | Rural Short | City of Kalgoorlie-Boulder | 21 | 299.8 | 202.5 | 2.38 | 2.09
BKF 611.0 ORA BANDA | Rural Short | Shire of Coolgardie | 7 | 656.3 | 202.5 | 5.21 | 2.09
BKF 611.0 ORA BANDA | Rural Short | Total | 28 | 391.4 | 202.5 | 3.11 | 2.09
BLD 619.0 PARINGA | Rural Long | Total - City of Kalgoorlie-Boulder | 129 | 1165.8 | 290.5 | 7.75 | 5.45
BLD 621.0 FIMISTON | Urban | Total - City of Kalgoorlie-Boulder | 30 | 1521.2 | 123.8 | 9.05 | 1.25
BNP 521.0 BEENUP | Rural Long | Shire of Augusta-Margaret River | 2446 | 279.8 | 290.5 | 2.34 | 5.45
BNP 521.0 BEENUP | Rural Long | Shire of Nannup | 58 | 1899.6 | 290.5 | 15.89 | 5.45
BNP 521.0 BEENUP | Rural Long | Total | 2504 | 316.9 | 290.5 | 2.65 | 5.45
BOD 507.0 ALCOA | Rural Long | Shire of Boddington | 985 | 402 | 290.5 | 2.35 | 5.45
BOD 507.0 ALCOA | Rural Long | Shire of Wandering | 80 | 523.1 | 290.5 | 3.05 | 5.45
BOD 507.0 ALCOA | Rural Long | Shire of Williams | 66 | 251.8 | 290.5 | 1.47 | 5.45
BOD 507.0 ALCOA | Rural Long | Total | 1131 | 405.4 | 290.5 | 2.36 | 5.45
BSN 505.0 LUDLOW | Rural Short | Total - City of Busselton | 2746 | 224 | 202.5 | 3.01 | 2.09
BSN 510.0 RENDEZVOUS | Rural Short | Total - City of Busselton | 2702 | 16.4 | 202.5 | 0.07 | 2.09
BSN 539.0 BUSSELTON | Rural Short | Total - City of Busselton | 4568 | 277.5 | 202.5 | 9.99 | 2.09
BSN 540.0 DUNSBOROUGH | Rural Short | Total - City of Busselton | 3559 | 456.9 | 202.5 | 6.32 | 2.09
BSN 546 BIRCHFIELDS | Rural Short | Total - City of Busselton | 3290 | 112.7 | 202.5 | 1.54 | 2.09
BSN 556.0 RENDEZVOUS RD RMU 3 | Rural Short | Total - City of Busselton | 3511 | 259.7 | 202.5 | 3.54 | 2.09
BSN 557.0 MARGARET RIVER | Rural Long | Total - City of Busselton | 3315 | 278.4 | 290.5 | 2.74 | 5.45
BTN 505.0 BOYUP BROOK | Rural Long | Shire of Boyup Brook | 1022 | 190.9 | 290.5 | 1.12 | 5.45
BTN 505.0 BOYUP BROOK | Rural Long | Shire of Bridgetown-Greenbushes | 507 | 214.1 | 290.5 | 1.25 | 5.45
BTN 505.0 BOYUP BROOK | Rural Long | Shire of West Arthur | 37 | 655.1 | 290.5 | 3.83 | 5.45
BTN 505.0 BOYUP BROOK | Rural Long | Total | 1584 | 209.2 | 290.5 | 1.22 | 5.45
BTN 511.0 BRIDGETOWN / KIRUP | Rural Long | Shire of Bridgetown-Greenbushes | 2375 | 237.3 | 290.5 | 3.66 | 5.45
BTN 511.0 BRIDGETOWN / KIRUP | Rural Long | Shire of Donnybrook-Balingup | 514 | 140.5 | 290.5 | 2.17 | 5.45
BTN 511.0 BRIDGETOWN / KIRUP | Rural Long | Total | 2889 | 220 | 290.5 | 3.39 | 5.45
BTN 516.0 GWALIA STH | Rural Long | Shire of Nannup | 1067 | 762.6 | 290.5 | 3.94 | 5.45
BTN 516.0 GWALIA STH | Rural Long | Shire of Bridgetown-Greenbushes | 93 | 211.5 | 290.5 | 1.09 | 5.45
BTN 516.0 GWALIA STH | Rural Long | Total | 1187 | 718.6 | 290.5 | 3.71 | 5.45
BTY 502.0 CHANNON ST | Urban | Total - City of Canning | 119 | 0.4 | 123.8 | 0.01 | 1.25
BTY 503.0 49 BOUNDARY RD RMU | Urban | City of Canning | 4062 | 8.2 | 123.8 | 0.16 | 1.25
BTY 503.0 49 BOUNDARY RD RMU | Urban | Town of Victoria Park | 1147 | 3.3 | 123.8 | 0.06 | 1.25
BTY 503.0 49 BOUNDARY RD RMU | Urban | Total | 5209 | 6.7 | 123.8 | 0.13 | 1.25
BTY 504.0 295 MANNING RD | Urban | Total - City of South Perth | 15 | 0 | 123.8 | 0 | 1.25
BTY 508.0 L4004 MANNING RD | Urban | City of Canning | 3146 | 12.9 | 123.8 | 0.14 | 1.25
BTY 508.0 L4004 MANNING RD | Urban | City of South Perth | 198 | 0 | 123.8 | 0 | 1.25
BTY 508.0 L4004 MANNING RD | Urban | Total | 3344 | 12 | 123.8 | 0.13 | 1.25
BTY 535.0 MILLS ST | Urban | Total - City of Canning | 1787 | 567.9 | 123.8 | 3.11 | 1.25
BTY 537.0 HILLVIEW TCE | Urban | Total - City of Canning | 848 | 462 | 123.8 | 15.9 | 1.25
BUH 511.0 HARBOUR NO.1 | Urban | Total - City of Bunbury | 1083 | 875.1 | 123.8 | 6.2 | 1.25
BUH 513.0 EATON-AUSTRALIND | Rural Short | Shire of Harvey | 3208 | 382.6 | 202.5 | 4.33 | 2.09
BUH 513.0 EATON-AUSTRALIND | Rural Short | City of Bunbury | 415 | 255.3 | 202.5 | 2.89 | 2.09
BUH 513.0 EATON-AUSTRALIND | Rural Short | Total | 3628 | 368.1 | 202.5 | 4.16 | 2.09
BUH 514.0 CAREY PARK | Urban | City of Bunbury | 3087 | 707.4 | 123.8 | 1.28 | 1.25
BUH 514.0 CAREY PARK | Urban | Shire of Capel | 1725 | 295.7 | 123.8 | 0.53 | 1.25
BUH 514.0 CAREY PARK | Urban | Total | 4812 | 562.7 | 123.8 | 1.02 | 1.25
BUH 517.0 AUSTRAL PDE | Urban | Total - City of Bunbury | 874 | 1961.9 | 123.8 | 2.04 | 1.25
BUH 522.0 BUNBURY CENTRAL | Urban | Total - City of Bunbury | 2907 | 637 | 123.8 | 2.16 | 1.25
BUH 525.0 BUNBURY SOUTH | Rural Short | City of Bunbury | 1991 | 90.7 | 202.5 | 3.05 | 2.09
BUH 525.0 BUNBURY SOUTH | Rural Short | Shire of Capel | 1520 | 100.6 | 202.5 | 3.38 | 2.09
BUH 525.0 BUNBURY SOUTH | Rural Short | Total | 3511 | 95.1 | 202.5 | 3.19 | 2.09
BUH 541.0 ROBERTSON DR | Urban | Total - City of Bunbury | 1328 | 86.8 | 123.8 | 1.86 | 1.25
BUH 551.0 BUNBURY NORTH | Urban | Total - City of Bunbury | 2283 | 54 | 123.8 | 0.92 | 1.25
BUH 552.0 SANDRIDGE RD | Urban | City of Bunbury | 2996 | 1239.2 | 123.8 | 2.96 | 1.25
BUH 552.0 SANDRIDGE RD | Urban | Shire of Capel | 1184 | 415.3 | 123.8 | 0.99 | 1.25
BUH 552.0 SANDRIDGE RD | Urban | Total | 4180 | 1036.3 | 123.8 | 2.48 | 1.25
BYF 503.0 ALEXANDER RMU | Urban | City of Armadale | 2360 | 267.5 | 123.8 | 1.93 | 1.25
BYF 503.0 ALEXANDER RMU | Urban | Shire of Serpentine-Jarrahdale | 988 | 114.6 | 123.8 | 0.83 | 1.25
BYF 503.0 ALEXANDER RMU | Urban | Total | 3348 | 218 | 123.8 | 1.57 | 1.25
BYF 504.0 L54 SOUTH WEST HWY | Urban | Total - Shire of Serpentine-Jarrahdale | 5525 | 289.6 | 123.8 | 2.89 | 1.25
BYF 505.0 L19 SOUTH WEST HWY | Rural Short | Total - Shire of Serpentine-Jarrahdale | 1690 | 377 | 202.5 | 3.16 | 2.09
BYF 508.0 843 SOUTH WESTERN HWY | Rural Short | Total - Shire of Serpentine-Jarrahdale | 1563 | 623.3 | 202.5 | 8.29 | 2.09
BYF 510.0 HIGHWAY NORTH | Rural Short | Total - City of Armadale | 2399 | 438.1 | 202.5 | 3.97 | 2.09
BYF 515.0 BUTCHER/THOMAS RD | Urban | City of Armadale | 7014 | 271.6 | 123.8 | 2.96 | 1.25
BYF 515.0 BUTCHER/THOMAS RD | Urban | Shire of Serpentine-Jarrahdale | 280 | 196.5 | 123.8 | 2.14 | 1.25
BYF 515.0 BUTCHER/THOMAS RD | Urban | Total | 7294 | 268.7 | 123.8 | 2.93 | 1.25
BYF 523.0 L4085 SUNRAYS ST | Rural Long | Total - Shire of Serpentine-Jarrahdale | 2632 | 214.4 | 290.5 | 3.75 | 5.45
BYF 524.0 L8004 ALEXANDER RD | Urban | Total - Shire of Serpentine-Jarrahdale | 103 | 83.1 | 123.8 | 0.95 | 1.25
BYF 527.0 L906 KARDAN BVD RMU | Rural Short | Total - City of Armadale | 1384 | 8.2 | 202.5 | 0.1 | 2.09
CAP 503.0 WONNERUP | Rural Long | City of Busselton | 638 | 868 | 290.5 | 4.27 | 5.45
CAP 503.0 WONNERUP | Rural Long | Shire of Capel | 45 | 1248.4 | 290.5 | 6.15 | 5.45
CAP 503.0 WONNERUP | Rural Long | Total | 684 | 881.9 | 290.5 | 4.34 | 5.45
CAP 509.0 YOGANUP | Rural Long | Shire of Donnybrook-Balingup | 1650 | 640.3 | 290.5 | 3.04 | 5.45
CAP 509.0 YOGANUP | Rural Long | Shire of Capel | 611 | 278.6 | 290.5 | 1.32 | 5.45
CAP 509.0 YOGANUP | Rural Long | Total | 2287 | 539 | 290.5 | 2.56 | 5.45
CAP 511.0 BOYANUP/CAPEL | Rural Long | Total - Shire of Capel | 2101 | 740.3 | 290.5 | 4.37 | 5.45
CAR 503.0 WALGOOLAN WATER CORP | Urban | Shire of Westonia | 143 | 810.6 | 123.8 | 2.83 | 1.25
CAR 503.0 WALGOOLAN WATER CORP | Urban | Shire of Merredin | 12 | 1599.8 | 123.8 | 5.58 | 1.25
CAR 503.0 WALGOOLAN WATER CORP | Urban | Total | 158 | 873.4 | 123.8 | 3.05 | 1.25
CC 501.0 RUSSELL RD WEST | Rural Short | City of Cockburn | 4469 | 279 | 202.5 | 3.68 | 2.09
CC 501.0 RUSSELL RD WEST | Rural Short | City of Kwinana | 423 | 46.7 | 202.5 | 0.62 | 2.09
CC 501.0 RUSSELL RD WEST | Rural Short | Total | 4892 | 265.9 | 202.5 | 3.51 | 2.09
CC 502.0 STATION RMU | Urban | Total - City of Cockburn | 1076 | 0 | 123.8 | 0 | 1.25
CC 505.0 CHANNEL CL | Urban | Total - City of Cockburn | 45 | 298.7 | 123.8 | 1.07 | 1.25
CC 507.0 HAMMOND RD | Rural Short | Total - City of Cockburn | 3269 | 179.6 | 202.5 | 1.21 | 2.09
CC 509.0 JERVOISE BAY | Urban | Total - City of Cockburn | 188 | 159.7 | 123.8 | 1.04 | 1.25
CC 515.0 RUSSELL RD EAST | Urban | Total - City of Cockburn | 3144 | 59.7 | 123.8 | 1.93 | 1.25
CC 516.0 11 SPARKS RD | Urban | Total - City of Cockburn | 42 | 3.9 | 123.8 | 0.02 | 1.25
CK 301.0 223 RUPERT ST/102 RAILWAY | Urban | City of Subiaco | 936 | 2.3 | 123.8 | 0.04 | 1.25
CK 301.0 223 RUPERT ST/102 RAILWAY | Urban | City of Perth | 24 | 0 | 123.8 | 0 | 1.25
CK 301.0 223 RUPERT ST/102 RAILWAY | Urban | Total | 960 | 2.3 | 123.8 | 0.04 | 1.25
CK 303.0 61 THOMAS ST | Urban | Town of Cambridge | 282 | 0.4 | 123.8 | 0 | 1.25
CK 303.0 61 THOMAS ST | Urban | City of Subiaco | 128 | 0 | 123.8 | 0 | 1.25
CK 303.0 61 THOMAS ST | Urban | City of Perth | 93 | 0 | 123.8 | 0 | 1.25
CK 303.0 61 THOMAS ST | Urban | Total | 503 | 0.2 | 123.8 | 0 | 1.25
CK 305.0 50 COLIN ST | Urban | City of Subiaco | 243 | 0 | 123.8 | 0 | 1.25
CK 305.0 50 COLIN ST | Urban | City of Perth | 73 | 0 | 123.8 | 0 | 1.25
CK 305.0 50 COLIN ST | Urban | Total | 316 | 0 | 123.8 | 0 | 1.25
CK 307.0 1008 WELLINGTON/16 RHEOLA | Urban | City of Perth | 811 | 0 | 123.8 | 0 | 1.25
CK 307.0 1008 WELLINGTON/16 RHEOLA | Urban | City of Subiaco | 70 | 0 | 123.8 | 0 | 1.25
CK 307.0 1008 WELLINGTON/16 RHEOLA | Urban | Total | 881 | 0 | 123.8 | 0 | 1.25
CK 311.0 1260 HAY ST | Urban | Total - City of Perth | 149 | 0 | 123.8 | 0 | 1.25
CK 313.0 PMH ZONE 1 | Urban | Total - City of Subiaco | 246 | 0 | 123.8 | 0 | 1.25
CK 316.0 L427 ROBERTS RD | Urban | City of Subiaco | 215 | 0 | 123.8 | 0 | 1.25
CK 316.0 L427 ROBERTS RD | Urban | City of Perth | 160 | 0 | 123.8 | 0 | 1.25
CK 316.0 L427 ROBERTS RD | Urban | Total | 375 | 0 | 123.8 | 0 | 1.25
CK 337.0 1195 HAY ST/THOMAS ST | Urban | Town of Cambridge | 854 | 117.1 | 123.8 | 1.71 | 1.25
CK 337.0 1195 HAY ST/THOMAS ST | Urban | City of Perth | 365 | 151.5 | 123.8 | 2.21 | 1.25
CK 337.0 1195 HAY ST/THOMAS ST | Urban | Total | 1219 | 127.9 | 123.8 | 1.86 | 1.25
CK 339.0 111 COLIN ST/1303 HAY ST | Urban | Total - City of Perth | 169 | 0 | 123.8 | 0 | 1.25
CK 341.0 1297 HAY ST/300 HAMERSLEY | Urban | City of Subiaco | 1274 | 0 | 123.8 | 0 | 1.25
CK 341.0 1297 HAY ST/300 HAMERSLEY | Urban | City of Perth | 120 | 6 | 123.8 | 0.01 | 1.25
CK 341.0 1297 HAY ST/300 HAMERSLEY | Urban | Total | 1394 | 0.5 | 123.8 | 0 | 1.25
CK 343.0 35 BARKER RD | Urban | City of Subiaco | 1498 | 37.2 | 123.8 | 1.21 | 1.25
CK 343.0 35 BARKER RD | Urban | Town of Cambridge | 450 | 37.2 | 123.8 | 1.21 | 1.25
CK 343.0 35 BARKER RD | Urban | Total | 1951 | 37.2 | 123.8 | 1.21 | 1.25
CK 347.0 1178 AND 1324 HAY ST | Urban | Total - City of Perth | 324 | 0 | 123.8 | 0 | 1.25
CK 349.0 90 ROBERTS RD | Urban | Total - City of Subiaco | 297 | 0 | 123.8 | 0 | 1.25
CK 352.0 69 OUTRAM ST | Urban | City of Subiaco | 822 | 0 | 123.8 | 0 | 1.25
CK 352.0 69 OUTRAM ST | Urban | City of Perth | 178 | 0 | 123.8 | 0 | 1.25
CK 352.0 69 OUTRAM ST | Urban | Total | 1000 | 0 | 123.8 | 0 | 1.25
CK 354.0 197 HAY ST | Urban | City of Subiaco | 813 | 23.5 | 123.8 | 0.07 | 1.25
CK 354.0 197 HAY ST | Urban | City of Perth | 553 | 0 | 123.8 | 0 | 1.25
CK 354.0 197 HAY ST | Urban | Total | 1366 | 14 | 123.8 | 0.04 | 1.25
CKN 504.0 81 TAPPING WAY | Urban | Total - City of Wanneroo | 2868 | 62.4 | 123.8 | 0.91 | 1.25
CKN 505.0 L1001 GLOBAL RD | Urban | Total - City of Wanneroo | 477 | 115.7 | 123.8 | 1.07 | 1.25
CKN 507.0 L8 MARMION AVE | Urban | Total - City of Wanneroo | 4344 | 270.5 | 123.8 | 2.75 | 1.25
CKN 508.0 BELLPORT 1 RMU | Urban | Total - City of Wanneroo | 3679 | 24 | 123.8 | 0.17 | 1.25
CKN 536.0 OPP 2 RIDGEWOOD BVD RMU | Urban | Total - City of Wanneroo | 3444 | 9.6 | 123.8 | 0.1 | 1.25
CKN 539.0 L229 WALYUNGA BVD | Urban | Total - City of Wanneroo | 2547 | 2.6 | 123.8 | 0.04 | 1.25
CKN 540.0 L476 HIDDEN VALLEY RTT | Urban | Total - City of Wanneroo | 4362 | 127.8 | 123.8 | 2.17 | 1.25
CL 303.0 180 MILL POINT RD | Urban | Total - City of South Perth | 733 | 49.9 | 123.8 | 0.38 | 1.25
CL 304.0 BERWICK ST | Rural Short | Town of Victoria Park | 1687 | 0 | 202.5 | 0 | 2.09
CL 304.0 BERWICK ST | Rural Short | City of South Perth | 137 | 0 | 202.5 | 0 | 2.09
CL 304.0 BERWICK ST | Rural Short | Total | 1824 | 0 | 202.5 | 0 | 2.09
CL 305.0 34 KAROO ST | Urban | Total - City of South Perth | 1290 | 2.7 | 123.8 | 0 | 1.25
CL 306.0 AMHERST ST B | Urban | Total - City of South Perth | 967 | 62.6 | 123.8 | 0.15 | 1.25
CL 311.0 YORK ST | Urban | Total - City of South Perth | 964 | 0.5 | 123.8 | 0 | 1.25
CL 312.0 45 FORREST/64 MILL POINT | Urban | Town of Victoria Park | 1393 | 400.2 | 123.8 | 3.75 | 1.25
CL 312.0 45 FORREST/64 MILL POINT | Urban | City of South Perth | 581 | 339.7 | 123.8 | 3.18 | 1.25
CL 312.0 45 FORREST/64 MILL POINT | Urban | Total | 1974 | 377.1 | 123.8 | 3.53 | 1.25
CL 315.0 AMHERST ST A | Urban | Total - City of South Perth | 1828 | 30.2 | 123.8 | 0.04 | 1.25
CL 316.0 155 MILL POINT RD | Urban | Total - City of South Perth | 1244 | 0.3 | 123.8 | 0 | 1.25
CLP 508.0 DWELLINGUP | Rural Short | Total - Shire of Murray | 65 | 0 | 202.5 | 0 | 2.09
CO 504.0 CARDIFF | Rural Long | Shire of Collie | 1025 | 50.1 | 290.5 | 0.92 | 5.45
CO 504.0 CARDIFF | Rural Long | Shire of Donnybrook-Balingup | 122 | 204.2 | 290.5 | 3.77 | 5.45
CO 504.0 CARDIFF | Rural Long | Total | 1176 | 66.5 | 290.5 | 1.23 | 5.45
CO 506.0 COLLIE BURN | Rural Short | Total - Shire of Collie | 605 | 48.9 | 202.5 | 1.44 | 2.09
CO 508.0 SHOTTS | Rural Short | Total - Shire of Collie | 442 | 124.8 | 202.5 | 2.38 | 2.09
CO 513.0 BINGHAM CREEK | Rural Short | Total - Shire of Collie | 2172 | 286.1 | 202.5 | 1.71 | 2.09
CO 515.0 ALWEST | Rural Short | Total - Shire of Collie | 98 | 20 | 202.5 | 0.35 | 2.09
CO 517.0 WELLINGTON DAM | Rural Short | Shire of Collie | 311 | 725.8 | 202.5 | 2.79 | 2.09
CO 517.0 WELLINGTON DAM | Rural Short | Shire of Dardanup | 24 | 934.8 | 202.5 | 3.59 | 2.09
CO 517.0 WELLINGTON DAM | Rural Short | Total | 335 | 741.3 | 202.5 | 2.85 | 2.09
COL 304.0 THROSSELL ST | Urban | Total - City of South Perth | 1496 | 17.5 | 123.8 | 0.1 | 1.25
COL 305.0 101 THELMA ST | Urban | Total - City of South Perth | 288 | 8.8 | 123.8 | 0.04 | 1.25
COL 307.0 17 DICK PARRY AVE | Urban | City of South Perth | 452 | 81 | 123.8 | 0.45 | 1.25
COL 307.0 17 DICK PARRY AVE | Urban | City of Canning | 348 | 82.1 | 123.8 | 0.46 | 1.25
COL 307.0 17 DICK PARRY AVE | Urban | Town of Victoria Park | 87 | 3.3 | 123.8 | 0.02 | 1.25
COL 307.0 17 DICK PARRY AVE | Urban | Total | 887 | 74.3 | 123.8 | 0.42 | 1.25
COL 308.0 RYRIE AVE | Urban | City of South Perth | 452 | 1.1 | 123.8 | 0.01 | 1.25
COL 308.0 RYRIE AVE | Urban | Town of Victoria Park | 108 | 0 | 123.8 | 0 | 1.25
COL 308.0 RYRIE AVE | Urban | Total | 560 | 0.9 | 123.8 | 0.01 | 1.25
COL 316.0 2 AXFORD ST | Urban | Total - City of South Perth | 1753 | 114.7 | 123.8 | 0.26 | 1.25
COL 317.0 40 CLYDESDALE ST | Urban | Total - City of South Perth | 1799 | 133.5 | 123.8 | 0.34 | 1.25
COL 326.0 101 THELMA ST 1 | Urban | Total - Town of Victoria Park | 743 | 2 | 123.8 | 0 | 1.25
COL 327.0 13 COLLINS ST | Urban | Total - City of South Perth | 1770 | 134.6 | 123.8 | 0.53 | 1.25
COL 335.0 1 MORRISON ST | Urban | Total - City of South Perth | 1324 | 76.5 | 123.8 | 0.12 | 1.25
COL 337.0 1 CLYDESDALE ST | Urban | Total - City of South Perth | 1806 | 0 | 123.8 | 0 | 1.25
COL 339.0 56 SAUNDERS ST | Urban | Total - City of South Perth | 2291 | 62.1 | 123.8 | 0.6 | 1.25
COL 340.0 OPP 24 MONASH AVE | Urban | City of South Perth | 578 | 0 | 123.8 | 0 | 1.25
COL 340.0 OPP 24 MONASH AVE | Urban | Town of Victoria Park | 285 | 0 | 123.8 | 0 | 1.25
COL 340.0 OPP 24 MONASH AVE | Urban | Total | 863 | 0 | 123.8 | 0 | 1.25
CPN 315.0 BLUFF POINT | Urban | Total - City of Greater Geraldton | 1192 | 12.9 | 123.8 | 0.12 | 1.25
CPN 316.0 WAGGRAKINE | Rural Short | Total - City of Greater Geraldton | 1225 | 606.5 | 202.5 | 1.21 | 2.09
CPN 318.0 504 N/WEST COASTAL HWY | Rural Short | Total - City of Greater Geraldton | 655 | 261.6 | 202.5 | 1.12 | 2.09
CPN 319.0 WEBBERTON | Rural Short | Total - City of Greater Geraldton | 678 | 130.6 | 202.5 | 1.22 | 2.09
CPN 326.0 SPALDING L/S | Urban | Total - City of Greater Geraldton | 794 | 1083 | 123.8 | 2.63 | 1.25
CPN 336.0 980 CHAPMAN RD | Rural Short | Total - City of Greater Geraldton | 963 | 1.8 | 202.5 | 0.01 | 2.09
CTE 302.0 14 ATHELSTAN RD | Urban | Town of Claremont | 541 | 0 | 123.8 | 0 | 1.25
CTE 302.0 14 ATHELSTAN RD | Urban | Town of Cottesloe | 394 | 0 | 123.8 | 0 | 1.25
CTE 302.0 14 ATHELSTAN RD | Urban | Total | 935 | 0 | 123.8 | 0 | 1.25
CTE 304.0 L24 VIEW ST | Urban | Town of Claremont | 367 | 121.6 | 123.8 | 0.55 | 1.25
CTE 304.0 L24 VIEW ST | Urban | Shire of Peppermint Grove | 76 | 12.5 | 123.8 | 0.06 | 1.25
CTE 304.0 L24 VIEW ST | Urban | Town of Cottesloe | 30 | 471.2 | 123.8 | 2.12 | 1.25
CTE 304.0 L24 VIEW ST | Urban | Total | 473 | 126.3 | 123.8 | 0.57 | 1.25
CTE 306.0 9 DEAN ST/120BROOM | Urban | Town of Cottesloe | 1449 | 20.1 | 123.8 | 0.07 | 1.25
CTE 306.0 9 DEAN ST/120BROOM | Urban | Town of Claremont | 956 | 0 | 123.8 | 0 | 1.25
CTE 306.0 9 DEAN ST/120BROOM | Urban | City of Nedlands | 269 | 144.8 | 123.8 | 0.47 | 1.25
CTE 306.0 9 DEAN ST/120BROOM | Urban | Total | 2674 | 30.8 | 123.8 | 0.1 | 1.25
CTE 309.0 183 CURTIN AVE/WELLINGTON | Urban | City of Fremantle | 1113 | 0.4 | 123.8 | 0 | 1.25
CTE 309.0 183 CURTIN AVE/WELLINGTON | Urban | Town of Mosman Park | 543 | 0.1 | 123.8 | 0 | 1.25
CTE 309.0 183 CURTIN AVE/WELLINGTON | Urban | Town of Cottesloe | 301 | 0 | 123.8 | 0 | 1.25
CTE 309.0 183 CURTIN AVE/WELLINGTON | Urban | Total | 1957 | 0.2 | 123.8 | 0 | 1.25
CTE 310.0 31 JARRAD ST | Urban | Shire of Peppermint Grove | 367 | 136.4 | 123.8 | 0.28 | 1.25
CTE 310.0 31 JARRAD ST | Urban | Town of Mosman Park | 191 | 14.3 | 123.8 | 0.03 | 1.25
CTE 310.0 31 JARRAD ST | Urban | Town of Cottesloe | 97 | 0 | 123.8 | 0 | 1.25
CTE 310.0 31 JARRAD ST | Urban | Total | 656 | 80.4 | 123.8 | 0.16 | 1.25
CTE 317.0 47 BROOME ST/1 STATION ST | Urban | Town of Cottesloe | 1545 | 0 | 123.8 | 0 | 1.25
CTE 317.0 47 BROOME ST/1 STATION ST | Urban | Town of Mosman Park | 284 | 0.3 | 123.8 | 0 | 1.25
CTE 317.0 47 BROOME ST/1 STATION ST | Urban | Shire of Peppermint Grove | 85 | 127.8 | 123.8 | 0.41 | 1.25
CTE 317.0 47 BROOME ST/1 STATION ST | Urban | Total | 1914 | 5.6 | 123.8 | 0.02 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | Town of Mosman Park | 915 | 0 | 123.8 | 0 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | City of Fremantle | 425 | 0 | 123.8 | 0 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | City of Nedlands | 242 | 0 | 123.8 | 0 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | Shire of Peppermint Grove | 56 | 0 | 123.8 | 0 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | Town of Claremont | 44 | 0 | 123.8 | 0 | 1.25
CTE 318.0 12 JOHNSTON ST / 99 NORTH | Urban | Total | 1683 | 0.1 | 123.8 | 0 | 1.25
CTE 321.0 L2549 LEAKE ST/UWA | Urban | Town of Claremont | 616 | 0.2 | 123.8 | 0 | 1.25
CTE 321.0 L2549 LEAKE ST/UWA | Urban | City of Nedlands | 66 | 0 | 123.8 | 0 | 1.25
CTE 321.0 L2549 LEAKE ST/UWA | Urban | Shire of Peppermint Grove | 60 | 0 | 123.8 | 0 | 1.25
CTE 321.0 L2549 LEAKE ST/UWA | Urban | Total | 743 | 0.1 | 123.8 | 0 | 1.25
CTE 322.0 611 STIRLING HWY | Urban | Town of Mosman Park | 1656 | 127.4 | 123.8 | 2.33 | 1.25
CTE 322.0 611 STIRLING HWY | Urban | Shire of Peppermint Grove | 49 | 94.8 | 123.8 | 1.74 | 1.25
CTE 322.0 611 STIRLING HWY | Urban | Total | 1709 | 126.5 | 123.8 | 2.32 | 1.25
CTE 324.0 52 GRANT ST RMU | Urban | Town of Claremont | 434 | 0 | 123.8 | 0 | 1.25
CTE 324.0 52 GRANT ST RMU | Urban | City of Nedlands | 393 | 0 | 123.8 | 0 | 1.25
CTE 324.0 52 GRANT ST RMU | Urban | Town of Cottesloe | 250 | 0 | 123.8 | 0 | 1.25
CTE 324.0 52 GRANT ST RMU | Urban | Total | 1078 | 0 | 123.8 | 0 | 1.25
CTE 326.0 OPP 9 LOCHEE ST | Urban | Total - Town of Mosman Park | 634 | 56.2 | 123.8 | 0.16 | 1.25
CUN 501.0 TAMMIN | Rural Long | Shire of Tammin | 246 | 1420 | 290.5 | 8.44 | 5.45
CUN 501.0 TAMMIN | Rural Long | Shire of Cunderdin | 40 | 530.9 | 290.5 | 3.15 | 5.45
CUN 501.0 TAMMIN | Rural Long | Shire of Wyalkatchem | 11 | 2931.3 | 290.5 | 17.42 | 5.45
CUN 501.0 TAMMIN | Rural Long | Total | 303 | 1352.2 | 290.5 | 8.03 | 5.45
CUN 502.0 MINNIVALE | Rural Long | Shire of Dowerin | 418 | 1087.4 | 290.5 | 11.88 | 5.45
CUN 502.0 MINNIVALE | Rural Long | Shire of Wyalkatchem | 405 | 1220.4 | 290.5 | 13.34 | 5.45
CUN 502.0 MINNIVALE | Rural Long | Shire of Koorda | 324 | 1339.4 | 290.5 | 14.64 | 5.45
CUN 502.0 MINNIVALE | Rural Long | Shire of Cunderdin | 60 | 3143.9 | 290.5 | 34.36 | 5.45
CUN 502.0 MINNIVALE | Rural Long | Total | 1233 | 1301.7 | 290.5 | 14.23 | 5.45
CUN 503.0 MECKERING | Rural Long | Total - Shire of Cunderdin | 618 | 785.9 | 290.5 | 6.21 | 5.45
CUN 506.0 QUAIRADING | Rural Long | Shire of Quairading | 629 | 3481.5 | 290.5 | 13.24 | 5.45
CUN 506.0 QUAIRADING | Rural Long | Shire of Cunderdin | 66 | 983.6 | 290.5 | 3.74 | 5.45
CUN 506.0 QUAIRADING | Rural Long | Shire of York | 21 | 2848.4 | 290.5 | 10.84 | 5.45
CUN 506.0 QUAIRADING | Rural Long | Shire of Beverley | 18 | 4205.6 | 290.5 | 16 | 5.45
CUN 506.0 QUAIRADING | Rural Long | Total | 752 | 3255.3 | 290.5 | 12.38 | 5.45
CVE 501.0 VELLGROVE AVE | Rural Short | Total - City of Canning | 3376 | 125.3 | 202.5 | 2.5 | 2.09
CVE 502.0 VULCAN RD EAST | Urban | City of Gosnells | 2044 | 2.5 | 123.8 | 0.02 | 1.25
CVE 502.0 VULCAN RD EAST | Urban | City of Canning | 46 | 28.9 | 123.8 | 0.23 | 1.25
CVE 502.0 VULCAN RD EAST | Urban | Total | 2090 | 3.1 | 123.8 | 0.02 | 1.25
CVE 503.0 CANVALE RD | Urban | Total - City of Gosnells | 3768 | 47.8 | 123.8 | 0.15 | 1.25
CVE 512.0 MAGNET RD WEST | Urban | City of Canning | 2318 | 151.5 | 123.8 | 1.43 | 1.25
CVE 512.0 MAGNET RD WEST | Urban | City of Gosnells | 1584 | 176.1 | 123.8 | 1.66 | 1.25
CVE 512.0 MAGNET RD WEST | Urban | Total | 3902 | 161.5 | 123.8 | 1.52 | 1.25
CVE 513.0 MAGNET RD EAST | Urban | Total - City of Canning | 2113 | 18.7 | 123.8 | 0.11 | 1.25
CVE 516.0 NICHOLSON RD | Urban | Total - City of Gosnells | 2056 | 0.1 | 123.8 | 0 | 1.25
CVE 517.0 COULSON WAY | Urban | Total - City of Canning | 183 | 30.5 | 123.8 | 0.12 | 1.25
CVE 522.0 VULCAN WEST | Urban | Total - City of Canning | 194 | 1083.5 | 123.8 | 25.77 | 1.25
CVE 524.0 77 VULCAN RD | Rural Short | Total - City of Canning | 47 | 0 | 202.5 | 0 | 2.09
CVE 527.0 HOPEWELL ST | Urban | Total - City of Canning | 68 | 0 | 123.8 | 0 | 1.25
CVE 529.0 BAILE SOUTH | Urban | Total - City of Canning | 25 | 0 | 123.8 | 0 | 1.25
D 504.0 DARLINGTON S/S RMU | Urban | Total - Shire of Mundaring | 813 | 331.2 | 123.8 | 2.03 | 1.25
D 516.0 VICTOR RD EAST | Rural Short | Shire of Mundaring | 1747 | 969.1 | 202.5 | 8.75 | 2.09
D 516.0 VICTOR RD EAST | Rural Short | City of Swan | 176 | 626.8 | 202.5 | 5.66 | 2.09
D 516.0 VICTOR RD EAST | Rural Short | Total | 1923 | 937.4 | 202.5 | 8.47 | 2.09
D 517.0 VICTOR RD WEST | Rural Short | Shire of Mundaring | 1277 | 63.6 | 202.5 | 1.3 | 2.09
D 517.0 VICTOR RD WEST | Rural Short | City of Swan | 450 | 48.7 | 202.5 | 1 | 2.09
D 517.0 VICTOR RD WEST | Rural Short | Total | 1758 | 60 | 202.5 | 1.23 | 2.09
D 525.0 DARLINGTON EAST | Rural Short | Total - Shire of Mundaring | 2789 | 511.2 | 202.5 | 4.88 | 2.09
E 302.0 HAMPTON/PHILLIMORE ST | Urban | Total - City of Fremantle | 902 | 9.2 | 123.8 | 0.07 | 1.25
E 303.0 AMHERST 1/21SOUTH ST | Urban | Total - City of Fremantle | 669 | 11.9 | 123.8 | 0.1 | 1.25
E 305.0 STEVEN ST | Urban | Total - City of Fremantle | 1156 | 47.9 | 123.8 | 0.16 | 1.25
E 309.0 HOSPITAL #1 | Urban | Total - City of Fremantle | 542 | 6.8 | 123.8 | 0.02 | 1.25
E 310.0 EAST FREMANTLE | Urban | City of Fremantle | 1696 | 0.7 | 123.8 | 0 | 1.25
E 310.0 EAST FREMANTLE | Urban | Town of East Fremantle | 520 | 0 | 123.8 | 0 | 1.25
E 310.0 EAST FREMANTLE | Urban | Total | 2216 | 0.5 | 123.8 | 0 | 1.25
E 311.0 FOTHERGILL NTH | Urban | Total - City of Fremantle | 398 | 2.9 | 123.8 | 0 | 1.25
E 316.0 SOUTH ST | Urban | Total - City of Fremantle | 2647 | 63.1 | 123.8 | 0.69 | 1.25
ENB 602.0 NORTH MINE | Rural Short | Shire of Carnamah | 9 | 1774.7 | 202.5 | 9.24 | 2.09
ENB 602.0 NORTH MINE | Rural Short | Shire of Coorow | 1 | 1259.3 | 202.5 | 6.55 | 2.09
ENB 602.0 NORTH MINE | Rural Short | Total | 10 | 1710.3 | 202.5 | 8.9 | 2.09
ENB 605.0 LEEMAN | Rural Short | Total - Shire of Coorow | 848 | 470.8 | 202.5 | 4.01 | 2.09
ENB 617.0 JURIEN | Rural Long | Shire of Dandaragan | 2610 | 1068.7 | 290.5 | 4.13 | 5.45
ENB 617.0 JURIEN | Rural Long | Shire of Coorow | 87 | 2766.8 | 290.5 | 10.69 | 5.45
ENB 617.0 JURIEN | Rural Long | Total | 2711 | 1124.4 | 290.5 | 4.34 | 5.45
FFD 501.0 FORRESTFIELD S/S RMU | Urban | Total - City of Kalamunda | 27 | 385.6 | 123.8 | 3.08 | 1.25
FFD 506.0 435 DUNDAS RD | Rural Short | Total - City of Kalamunda | 3558 | 134 | 202.5 | 3.68 | 2.09
FFD 517.0 10 IBIS PL 2 | Urban | Total - City of Kalamunda | 75 | 23.7 | 123.8 | 0.06 | 1.25
FFD 525.0 1 BEYER PL | Urban | Total - City of Kalamunda | 45 | 0 | 123.8 | 0 | 1.25
FFD 536.0 471 DUNDAS RD | Urban | Total - City of Kalamunda | 2863 | 39 | 123.8 | 1.01 | 1.25
G 502.0 TERENCE STREET | Urban | City of Armadale | 1437 | 82.8 | 123.8 | 1.84 | 1.25
G 502.0 TERENCE STREET | Urban | City of Gosnells | 715 | 158.2 | 123.8 | 3.51 | 1.25
G 502.0 TERENCE STREET | Urban | Total | 2152 | 108 | 123.8 | 2.39 | 1.25
G 504.0 24 EUDORIA ST | Urban | Total - City of Gosnells | 3451 | 90.7 | 123.8 | 3.37 | 1.25
G 506.0 WALTER WEST | Urban | Total - City of Gosnells | 3812 | 39.1 | 123.8 | 0.15 | 1.25
G 508.0 CRANDON NORTH | Urban | Total - City of Gosnells | 2007 | 99.1 | 123.8 | 0.65 | 1.25
G 514.0 CRANDON SOUTH | Urban | Total - City of Gosnells | 4549 | 255.5 | 123.8 | 2.92 | 1.25
G 515.0 | Rural Short | City of Armadale | 2647 | 639.9 | 202.5 | 5.91 | 2.09
G 515.0 | Rural Short | City of Gosnells | 363 | 409.3 | 202.5 | 3.78 | 2.09
G 515.0 | Rural Short | Total | 3011 | 612.4 | 202.5 | 5.65 | 2.09
G 518.0 CORFIELD NORTH | Urban | Total - City of Gosnells | 2881 | 230.4 | 123.8 | 1.67 | 1.25
G 520.0 5 STALKER RD | Urban | Total - City of Gosnells | 1242 | 93.6 | 123.8 | 2.15 | 1.25
G 522.0 85 WHEATLEY ST | Urban | City of Armadale | 1445 | 17.1 | 123.8 | 0.16 | 1.25
G 522.0 85 WHEATLEY ST | Urban | City of Gosnells | 961 | 0.2 | 123.8 | 0 | 1.25
G 522.0 85 WHEATLEY ST | Urban | Total | 2406 | 10.3 | 123.8 | 0.1 | 1.25
GTN 603.0 KALBARRI | Rural Long | Total - Shire of Chapman Valley | 12 | 170 | 290.5 | 6.16 | 5.45
GTN 646.0 KALBARRI | Rural Long | Shire of Northampton | 1403 | 1275.1 | 290.5 | 9.21 | 5.45
GTN 646.0 KALBARRI | Rural Long | City of Greater Geraldton | 447 | 602.3 | 290.5 | 4.35 | 5.45
GTN 646.0 KALBARRI | Rural Long | Shire of Chapman Valley | 421 | 657.7 | 290.5 | 4.75 | 5.45
GTN 646.0 KALBARRI | Rural Long | Total | 2271 | 1008.2 | 290.5 | 7.28 | 5.45
GTN 647.0 NORTHAMPTON | Rural Long | Shire of Northampton | 1047 | 1756.7 | 290.5 | 6.35 | 5.45
GTN 647.0 NORTHAMPTON | Rural Long | City of Greater Geraldton | 387 | 1588.8 | 290.5 | 5.74 | 5.45
GTN 647.0 NORTHAMPTON | Rural Long | Shire of Chapman Valley | 362 | 2480.5 | 290.5 | 8.96 | 5.45
GTN 647.0 NORTHAMPTON | Rural Long | Total | 1796 | 1866.7 | 290.5 | 6.74 | 5.45
GTN 651.0 NARNGULU EAST | Urban | Total - City of Greater Geraldton | 84 | 7134.6 | 123.8 | 22.63 | 1.25
GTN 653.0 DONGARA | Rural Long | City of Greater Geraldton | 808 | 1783.8 | 290.5 | 9.17 | 5.45
GTN 653.0 DONGARA | Rural Long | Shire of Irwin | 417 | 3915.2 | 290.5 | 20.13 | 5.45
GTN 653.0 DONGARA | Rural Long | Total | 1239 | 2511.6 | 290.5 | 12.91 | 5.45
GTN 665.0 NARNGULU WEST | Rural Long | Shire of Irwin | 1951 | 773.3 | 290.5 | 13.8 | 5.45
GTN 665.0 NARNGULU WEST | Rural Long | City of Greater Geraldton | 597 | 1386.2 | 290.5 | 24.73 | 5.45
GTN 665.0 NARNGULU WEST | Rural Long | Total | 2548 | 915.9 | 290.5 | 16.34 | 5.45
GTN 666.0 MULLEWA | Rural Long | City of Greater Geraldton | 972 | 3897.5 | 290.5 | 13.96 | 5.45
GTN 666.0 MULLEWA | Rural Long | Shire of Chapman Valley | 31 | 10828.1 | 290.5 | 38.8 | 5.45
GTN 666.0 MULLEWA | Rural Long | Total | 1004 | 4112.6 | 290.5 | 14.74 | 5.45
H 502.0 IOLANTHE ST | Urban | Town of Bassendean | 3174 | 223.7 | 123.8 | 1.98 | 1.25
H 502.0 IOLANTHE ST | Urban | City of Swan | 1672 | 331.5 | 123.8 | 2.93 | 1.25
H 502.0 IOLANTHE ST | Urban | City of Bayswater | 513 | 289.7 | 123.8 | 2.56 | 1.25
H 502.0 IOLANTHE ST | Urban | Total | 5359 | 260.8 | 123.8 | 2.3 | 1.25
H 504.0 COLLIER RD | Urban | Town of Bassendean | 240 | 337.7 | 123.8 | 1.44 | 1.25
H 504.0 COLLIER RD | Urban | City of Bayswater | 55 | 192.7 | 123.8 | 0.82 | 1.25
H 504.0 COLLIER RD | Urban | Total | 295 | 311.4 | 123.8 | 1.33 | 1.25
H 508.0 L268 PROSPECTOR LP | Urban | City of Swan | 1125 | 175.1 | 123.8 | 1 | 1.25
H 508.0 L268 PROSPECTOR LP | Urban | Town of Bassendean | 707 | 0.9 | 123.8 | 0 | 1.25
H 508.0 L268 PROSPECTOR LP | Urban | Total | 1832 | 114.9 | 123.8 | 0.66 | 1.25
H 510.0 RAILWAY PARADE WEST | Urban | Town of Bassendean | 23 | 0 | 123.8 | 0 | 1.25
H 510.0 RAILWAY PARADE WEST | Urban | City of Bayswater | 2 | 0 | 123.8 | 0 | 1.25
H 510.0 RAILWAY PARADE WEST | Urban | Total | 25 | 0 | 123.8 | 0 | 1.25
H 511.0 GERALDINE ST | Urban | Town of Bassendean | 2107 | 168.5 | 123.8 | 1.11 | 1.25
H 511.0 GERALDINE ST | Urban | City of Bayswater | 1138 | 248 | 123.8 | 1.64 | 1.25
H 511.0 GERALDINE ST | Urban | Total | 3245 | 203 | 123.8 | 1.34 | 1.25
H 514.0 SCADDEN ST | Urban | City of Bayswater | 2944 | 267.2 | 123.8 | 1.28 | 1.25
H 514.0 SCADDEN ST | Urban | Town of Bassendean | 564 | 295.1 | 123.8 | 1.42 | 1.25
H 514.0 SCADDEN ST | Urban | Total | 3508 | 271.7 | 123.8 | 1.3 | 1.25
H 516.0 249 COLLIER ST | Urban | Total - City of Bayswater | 1636 | 179.8 | 123.8 | 0.89 | 1.25
H 517.0 PALMERSTON ST | Urban | Town of Bassendean | 1327 | 55.1 | 123.8 | 0.22 | 1.25
H 517.0 PALMERSTON ST | Urban | City of Swan | 279 | 247.5 | 123.8 | 0.98 | 1.25
H 517.0 PALMERSTON ST | Urban | Total | 1617 | 88.7 | 123.8 | 0.35 | 1.25
HAY 303.0 50 MURRAY ST/IRWIN CHMBRS | CBD | Total - City of Perth | 47 | 59.5 | 13.7 | 1.96 | 0.21
HAY 305.0 219 ST GEORGES TCE | CBD | Total - City of Perth | 287 | 54.6 | 13.7 | 1.01 | 0.21
HAY 306.0 300 MURRAY ST 1 | CBD | Total - City of Perth | 43 | 61.2 | 13.7 | 1.1 | 0.21
HAY 307.0 FIRE BRGDE HQ/3 THE ESPLA | CBD | Total - City of Perth | 747 | 104 | 13.7 | 1.15 | 0.21
HAY 312.0 556 HAY/6 MOUNTS BAY Z2 | CBD | Total - City of Perth | 68 | 31.9 | 13.7 | 1.08 | 0.21
HAY 314.0 379 HAY/197 ST GEO ZONE B | CBD | Total - City of Perth | 100 | 57.8 | 13.7 | 1 | 0.21
HAY 316.0 713 HAY/19 PIER ST | CBD | Total - City of Perth | 46 | 33 | 13.7 | 1.1 | 0.21
HAY 318.0 32 ST.GEO.TCE/647 HAY ST | CBD | Total - City of Perth | 38 | 38.9 | 13.7 | 1.29 | 0.21
HAY 321.0 152-158 ST GEO TCE ZON-A | CBD | Total - City of Perth | 39 | 35.4 | 13.7 | 1 | 0.21
HAY 323.0 98 PIER ST | CBD | Total - City of Perth | 45 | 38.8 | 13.7 | 1 | 0.21
HAY 325.0 37 PIER ST / 517 HAY ST | CBD | Total - City of Perth | 119 | 74.3 | 13.7 | 0.43 | 0.21
HAY 334.0 445 HAY/38 MOUNTS BAY RD | CBD | Total - City of Perth | 469 | 63 | 13.7 | 1.01 | 0.21
HAY 336.0 30 THE ESPLND/18 MOUNT ST | CBD | Total - City of Perth | 26 | 870.8 | 13.7 | 2.09 | 0.21
HAY 337.0 109 MURRAY ST | CBD | Total - City of Perth | 26 | 20.4 | 13.7 | 1.04 | 0.21
HAY 339.0 200 MURRAY ST/125 MURRAY | CBD | Total - City of Perth | 70 | 22.8 | 13.7 | 1.09 | 0.21
HAY 341.0 565 HAY ST | CBD | Total - City of Perth | 234 | 22.8 | 13.7 | 1.05 | 0.21
HAY 343.0 HYATT WEST/ 25 BARRACK ST | CBD | Total - City of Perth | 188 | 23.3 | 13.7 | 1.03 | 0.21
HAY 347.0 197 ST GEO 138 BARRACK ST | CBD | Total - City of Perth | 67 | 24.7 | 13.7 | 1.97 | 0.21
HAY 349.0 152-158 ST GEO TCE ZONE B | CBD | Total - City of Perth | 84 | 35.8 | 13.7 | 1 | 0.21
HBK 504.0 LORD ST SOUTH | Urban | Total - City of Swan | 3195 | 72.6 | 123.8 | 0.66 | 1.25
HBK 507.0 2 WOOLLYBUSH RD | Rural Short | Total - City of Swan | 2649 | 1.1 | 202.5 | 0.01 | 2.09
HBK 508.0 20 BARRAMBIE WAY | Urban | Total - City of Swan | 3039 | 82.7 | 123.8 | 3.83 | 1.25
HBK 536.0 RIVERINA 1 RMU | Urban | Total - City of Swan | 3130 | 13.4 | 123.8 | 0.54 | 1.25
HBK 537.0 L456 SWANLEIGH PDE | Rural Short | Total - City of Swan | 7896 | 0.2 | 202.5 | 0 | 2.09
HBK 539.0 LISBON PL | Urban | Total - City of Swan | 1058 | 37.3 | 123.8 | 0.13 | 1.25
HZM 504.0 L80 BUSHMEAD | Urban | Total - City of Swan | 1861 | 224.4 | 123.8 | 1.62 | 1.25
HZM 505.0 BUSHMEAD RD | Urban | City of Kalamunda | 485 | 265.1 | 123.8 | 2.31 | 1.25
HZM 505.0 BUSHMEAD RD | Urban | City of Swan | 153 | 283.3 | 123.8 | 2.47 | 1.25
HZM 505.0 BUSHMEAD RD | Urban | Total | 638 | 269.5 | 123.8 | 2.35 | 1.25
HZM 507.0 71 BUSHMEAD RD | Rural Short | Shire of Mundaring | 1388 | 6.5 | 202.5 | 0.03 | 2.09
HZM 507.0 71 BUSHMEAD RD | Rural Short | City of Kalamunda | 1065 | 0.6 | 202.5 | 0 | 2.09
HZM 507.0 71 BUSHMEAD RD | Rural Short | City of Swan | 497 | 24.2 | 202.5 | 0.1 | 2.09
HZM 507.0 71 BUSHMEAD RD | Rural Short | Total | 2951 | 7.2 | 202.5 | 0.03 | 2.09
JDP 504.0 L2 SHENTON AVE | Urban | Total - City of Joondalup | 1891 | 47.9 | 123.8 | 1.1 | 1.25
JDP 505.0 4 NEWMARKET RTT | Urban | Total - City of Joondalup | 3017 | 12.8 | 123.8 | 0.07 | 1.25
JDP 507.0 ECU SWITCHROOM 2 | Rural Short | Total - City of Joondalup | 899 | 56 | 202.5 | 0.07 | 2.09
JDP 508.0 90 SHENTON AVE | Urban | Total - City of Joondalup | 967 | 0 | 123.8 | 0 | 1.25
JDP 536.0 BURNS BEACH RD | Urban | Total - City of Joondalup | 2789 | 1.1 | 123.8 | 0 | 1.25
JDP 539.0 JOONDALUP DR | Urban | Total - City of Joondalup | 890 | 10.2 | 123.8 | 0.1 | 1.25
JDP 540.0 MOORE DR | Urban | Total - City of Joondalup | 1157 | 3.1 | 123.8 | 0.01 | 1.25
JTE 302.0 WPC CENT CNTRL/65 FORREST | Urban | Total - City of Perth | 1887 | 107.6 | 123.8 | 0.07 | 1.25
JTE 304.0 48 JOEL TCE | Urban | City of Bayswater | 331 | 128.9 | 123.8 | 0.71 | 1.25
JTE 304.0 48 JOEL TCE | Urban | City of Vincent | 270 | 1.8 | 123.8 | 0.01 | 1.25
JTE 304.0 48 JOEL TCE | Urban | Total | 601 | 71.7 | 123.8 | 0.4 | 1.25
JTE 306.0 140 ROYAL ST ZONE B | Urban | Total - City of Perth | 622 | 0 | 123.8 | 0 | 1.25
JTE 307.0 65 FORREST AV RMU 4 | Urban | Total - City of Perth | 1108 | 1 | 123.8 | 0 | 1.25
JTE 310.0 45 PAKENHAM ST | Urban | City of Bayswater | 2110 | 32.4 | 123.8 | 0.13 | 1.25
JTE 310.0 45 PAKENHAM ST | Urban | City of Vincent | 94 | 0 | 123.8 | 0 | 1.25
JTE 310.0 45 PAKENHAM ST | Urban | Total | 2204 | 31.3 | 123.8 | 0.12 | 1.25
JTE 312.0 126 WHATLEY CR | Urban | City of Bayswater | 931 | 282.2 | 123.8 | 0.33 | 1.25
JTE 312.0 126 WHATLEY CR | Urban | City of Stirling | 532 | 0 | 123.8 | 0 | 1.25
JTE 312.0 126 WHATLEY CR | Urban | Total | 1463 | 180 | 123.8 | 0.21 | 1.25
JTE 315.0 65 FORREST AV RMU 5 | Urban | Total - City of Perth | 381 | 98.3 | 123.8 | 0.42 | 1.25
JTE 321.0 282 LORD ST | Urban | Total - City of Vincent | 2018 | 26 | 123.8 | 0.18 | 1.25
JTE 323.0 29 WEST PDE | Urban | City of Vincent | 1017 | 0.1 | 123.8 | 0 | 1.25
JTE 323.0 29 WEST PDE | Urban | City of Stirling | 483 | 3.8 | 123.8 | 0.05 | 1.25
JTE 323.0 29 WEST PDE | Urban | Total | 1501 | 1.3 | 123.8 | 0.02 | 1.25
JTE 325.0 139 RLWY PDE/65 FORREST | Urban | City of Stirling | 1623 | 5.1 | 123.8 | 0.01 | 1.25
JTE 325.0 139 RLWY PDE/65 FORREST | Urban | City of Perth | 347 | 0 | 123.8 | 0 | 1.25
JTE 325.0 139 RLWY PDE/65 FORREST | Urban | Total | 1970 | 4.2 | 123.8 | 0.01 | 1.25
JTE 327.0 298 LORD ST | Urban | Total - City of Vincent | 76 | 0 | 123.8 | 0 | 1.25
JTE 330.0 L405 EIGHT AVE | Urban | Total - City of Bayswater | 1501 | 86.9 | 123.8 | 0.52 | 1.25
JTE 332.0 103 SUMMERS ST | Urban | Total - City of Vincent | 284 | 495.2 | 123.8 | 8.44 | 1.25
JTE 335.0 71 EAST PDE/65 FORREST AV | Urban | Total - City of Perth | 585 | 6.7 | 123.8 | 0.04 | 1.25
JTE 337.0 211 PENINSULA RD | Urban | City of Bayswater | 2247 | 159.1 | 123.8 | 0.65 | 1.25
JTE 337.0 211 PENINSULA RD | Urban | City of Perth | 294 | 0 | 123.8 | 0 | 1.25
JTE 337.0 211 PENINSULA RD | Urban | Total | 2541 | 137.6 | 123.8 | 0.56 | 1.25
K 502.0 LEWIS RD EAST | Rural Short | Total - City of Kalamunda | 967 | 102.2 | 202.5 | 1.07 | 2.09
K 504.0 GUPPY RD/HOSPITAL | Rural Short | Total - City of Kalamunda | 2983 | 141.2 | 202.5 | 0.48 | 2.09
K 507.0 LEWIS W | Urban | Total - City of Kalamunda | 3435 | 188.1 | 123.8 | 3.59 | 1.25
K 515.0 PAULINE AVE | Urban | Total - City of Kalamunda | 1222 | 159 | 123.8 | 1.25 | 1.25
K 517.0 LESMURDIE AVE | Rural Short | Total - City of Kalamunda | 1947 | 97.4 | 202.5 | 0.57 | 2.09
K 520.0 GLADSTONE RD | Rural Short | City of Kalamunda | 577 | 256.8 | 202.5 | 2.05 | 2.09
K 520.0 GLADSTONE RD | Rural Short | City of Armadale | 185 | 1265.8 | 202.5 | 10.09 | 2.09
K 520.0 GLADSTONE RD | Rural Short | Total | 762 | 500.3 | 202.5 | 3.99 | 2.09
KAT 503.0 WOODANILLING | Rural Long | Shire of Woodanilling | 259 | 278.4 | 290.5 | 5.59 | 5.45
KAT 503.0 WOODANILLING | Rural Long | Shire of Katanning | 113 | 53.6 | 290.5 | 1.08 | 5.45
KAT 503.0 WOODANILLING | Rural Long | Shire of Kojonup | 28 | 903.3 | 290.5 | 18.14 | 5.45
KAT 503.0 WOODANILLING | Rural Long | Shire of West Arthur | 13 | 788.1 | 290.5 | 15.83 | 5.45
KAT 503.0 WOODANILLING | Rural Long | Total | 418 | 274.7 | 290.5 | 5.52 | 5.45
KAT 505.0 KOJONUP | Rural Short | Shire of Kojonup | 48 | 1127.9 | 202.5 | 5.45 | 2.09
KAT 505.0 KOJONUP | Rural Short | Shire of Katanning | 27 | 631.7 | 202.5 | 3.06 | 2.09
KAT 505.0 KOJONUP | Rural Short | Shire of Broomehill-Tambellup | 22 | 432.7 | 202.5 | 2.09 | 2.09
KAT 505.0 KOJONUP | Rural Short | Total | 97 | 832.8 | 202.5 | 4.03 | 2.09
KAT 506.0 TAMBELLUP | Rural Long | Shire of Broomehill-Tambellup | 643 | 254.4 | 290.5 | 1.35 | 5.45
KAT 506.0 TAMBELLUP | Rural Long | Shire of Gnowangerup | 453 | 236.3 | 290.5 | 1.26 | 5.45
KAT 506.0 TAMBELLUP | Rural Long | Shire of Kojonup | 34 | 434.3 | 290.5 | 2.31 | 5.45
KAT 506.0 TAMBELLUP | Rural Long | Total | 1164 | 252.5 | 290.5 | 1.34 | 5.45
KAT 509.0 GNOWANGERUP | Rural Long | Shire of Ravensthorpe | 472 | 1187.5 | 290.5 | 6.56 | 5.45
KAT 509.0 GNOWANGERUP | Rural Long | Shire of Gnowangerup | 421 | 1731.7 | 290.5 | 9.57 | 5.45
KAT 509.0 GNOWANGERUP | Rural Long | Shire of Jerramungup | 159 | 1830.9 | 290.5 | 10.11 | 5.45
KAT 509.0 GNOWANGERUP | Rural Long | Shire of Lake Grace | 137 | 3632 | 290.5 | 20.06 | 5.45
KAT 509.0 GNOWANGERUP | Rural Long | Total | 1215 | 1745.6 | 290.5 | 9.64 | 5.45
KAT 512.0 NYABING | Rural Long | Shire of Kent | 409 | 630.6 | 290.5 | 2.5 | 5.45
KAT 512.0 NYABING | Rural Long | Shire of Jerramungup | 212 | 12.4 | 290.5 | 0.05 | 5.45
KAT 512.0 NYABING | Rural Long | Shire of Katanning | 159 | 145.8 | 290.5 | 0.58 | 5.45
KAT 512.0 NYABING | Rural Long | Shire of Lake Grace | 43 | 775.2 | 290.5 | 3.07 | 5.45
KAT 512.0 NYABING | Rural Long | Total | 844 | 387.4 | 290.5 | 1.54 | 5.45
KAT 514.0 KATANNING | Rural Short | Total - Shire of Katanning | 1963 | 7.8 | 202.5 | 0.06 | 2.09
KDL 504.0 L536 ABERNETHY RD (1) | Urban | City of Belmont | 74 | 0.6 | 123.8 | 0.01 | 1.25
KDL 504.0 L536 ABERNETHY RD (1) | Urban | City of Canning | 6 | 0 | 123.8 | 0 | 1.25
KDL 504.0 L536 ABERNETHY RD (1) | Urban | Total | 80 | 0.6 | 123.8 | 0.01 | 1.25
KDL 505.0 MACKAY ST | Urban | City of Belmont | 95 | 184.3 | 123.8 | 1.39 | 1.25
KDL 505.0 MACKAY ST | Urban | City of Kalamunda | 85 | 170.7 | 123.8 | 1.29 | 1.25
KDL 505.0 MACKAY ST | Urban | Total | 180 | 177.9 | 123.8 | 1.34 | 1.25
KDL 507.0 HAZLEHURST ST | Urban | Total - City of Belmont | 36 | 80.8 | 123.8 | 2.02 | 1.25
KDL 536.0 495 ABERNETHY RD | Urban | Total - City of Belmont | 72 | 13.6 | 123.8 | 0.12 | 1.25
KDL 539.0 493 ABERNETHY RD | Urban | City of Belmont | 2265 | 107.4 | 123.8 | 0.3 | 1.25
KDL 539.0 493 ABERNETHY RD | Urban | Town of Victoria Park | 375 | 75.2 | 123.8 | 0.21 | 1.25
KDL 539.0 493 ABERNETHY RD | Urban | City of Canning | 149 | 91.6 | 123.8 | 0.26 | 1.25
KDL 539.0 493 ABERNETHY RD | Urban | Total | 2789 | 102.2 | 123.8 | 0.29 | 1.25
KDL 540.0 6 Hodgson Way | Urban | City of Belmont | 1086 | 722.1 | 123.8 | 11.37 | 1.25
KDL 540.0 6 Hodgson Way | Urban | City of Canning | 96 | 1286.2 | 123.8 | 20.25 | 1.25
KDL 540.0 6 Hodgson Way | Urban | Total | 1183 | 767.3 | 123.8 | 12.08 | 1.25
KDN 603.0 CORRIGIN | Rural Long | Shire of Corrigin | 712 | 1207.1 | 290.5 | 8.49 | 5.45
KDN 603.0 CORRIGIN | Rural Long | Shire of Bruce Rock | 84 | 1330 | 290.5 | 9.36 | 5.45
KDN 603.0 CORRIGIN | Rural Long | Total | 808 | 1220.2 | 290.5 | 8.58 | 5.45
KDN 605.0 NARAMBEEN | Rural Long | Shire of Narembeen | 574 | 1583.1 | 290.5 | 8.84 | 5.45
KDN 605.0 NARAMBEEN | Rural Long | Shire of Bruce Rock | 24 | 1243.9 | 290.5 | 6.95 | 5.45
KDN 605.0 NARAMBEEN | Rural Long | Shire of Corrigin | 17 | 4898.7 | 290.5 | 27.36 | 5.45
KDN 605.0 NARAMBEEN | Rural Long | Shire of Kondinin | 17 | 2171.6 | 290.5 | 12.13 | 5.45
KDN 605.0 NARAMBEEN | Rural Long | Total | 639 | 1676.6 | 290.5 | 9.36 | 5.45
KDN 606.0 HYDEN | Rural Long | Shire of Kondinin | 385 | 3194.4 | 290.5 | 9.21 | 5.45
KDN 606.0 HYDEN | Rural Long | Shire of Lake Grace | 59 | 3171.7 | 290.5 | 9.14 | 5.45
KDN 606.0 HYDEN | Rural Long | Shire of Kulin | 57 | 3847 | 290.5 | 11.09 | 5.45
KDN 606.0 HYDEN | Rural Long | Total | 501 | 3266.4 | 290.5 | 9.41 | 5.45
KDN 610.0 LAKE GRACE | Rural Long | Shire of Lake Grace | 839 | 1028.8 | 290.5 | 5.37 | 5.45
KDN 610.0 LAKE GRACE | Rural Long | Shire of Kulin | 69 | 1783.1 | 290.5 | 9.31 | 5.45
KDN 610.0 LAKE GRACE | Rural Long | Shire of Dumbleyung | 29 | 490.4 | 290.5 | 2.56 | 5.45
KDN 610.0 LAKE GRACE | Rural Long | Shire of Kondinin | 24 | 1253.8 | 290.5 | 6.55 | 5.45
KDN 610.0 LAKE GRACE | Rural Long | Total | 961 | 1072.3 | 290.5 | 5.6 | 5.45
KDN 611.0 KULIN | Rural Long | Shire of Kulin | 422 | 1101 | 290.5 | 6.68 | 5.45
KDN 611.0 KULIN | Rural Long | Shire of Wickepin | 378 | 3156.4 | 290.5 | 19.14 | 5.45
KDN 611.0 KULIN | Rural Long | Shire of Kondinin | 213 | 579.4 | 290.5 | 3.51 | 5.45
KDN 611.0 KULIN | Rural Long | Total | 1047 | 1487.6 | 290.5 | 9.02 | 5.45
KEL 502.0 SHACKLETON | Rural Long | Shire of Bruce Rock | 29 | 1415.7 | 290.5 | 3.85 | 5.45
KEL 502.0 SHACKLETON | Rural Long | Shire of Quairading | 28 | 2230.6 | 290.5 | 6.06 | 5.45
KEL 502.0 SHACKLETON | Rural Long | Shire of Kellerberrin | 21 | 461.2 | 290.5 | 1.25 | 5.45
KEL 502.0 SHACKLETON | Rural Long | Total | 78 | 1446.3 | 290.5 | 3.93 | 5.45
KEL 503.0 DOODLAKINE | Rural Short | Shire of Kellerberrin | 76 | 693.1 | 202.5 | 4.48 | 2.09
KEL 503.0 DOODLAKINE | Rural Short | Shire of Merredin | 14 | 1101.5 | 202.5 | 7.11 | 2.09
KEL 503.0 DOODLAKINE | Rural Short | Shire of Bruce Rock | 3 | 1120.8 | 202.5 | 7.24 | 2.09
KEL 503.0 DOODLAKINE | Rural Short | Total | 94 | 770.9 | 202.5 | 4.98 | 2.09
KEL 505.0 TRAYNING | Rural Long | Shire of Trayning | 305 | 512.7 | 290.5 | 3.61 | 5.45
KEL 505.0 TRAYNING | Rural Long | Shire of Kellerberrin | 62 | 2016 | 290.5 | 14.18 | 5.45
KEL 505.0 TRAYNING | Rural Long | Shire of Nungarin | 19 | 1575.4 | 290.5 | 11.08 | 5.45
KEL 505.0 TRAYNING | Rural Long | Total | 388 | 803.8 | 290.5 | 5.65 | 5.45
KEL 508.0 KELLERBERRIN | Rural Short | Shire of Kellerberrin | 559 | 350.9 | 202.5 | 4.37 | 2.09
KEL 508.0 KELLERBERRIN | Rural Short | Shire of Tammin | 16 | 1065.9 | 202.5 | 13.26 | 2.09
KEL 508.0 KELLERBERRIN | Rural Short | Total | 575 | 370.2 | 202.5 | 4.61 | 2.09
KOJ 504.0 MURADUP | Rural Long | Shire of Kojonup | 153 | 217.1 | 290.5 | 1.89 | 5.45
KOJ 504.0 MURADUP | Rural Long | Shire of Boyup Brook | 72 | 401.6 | 290.5 | 3.5 | 5.45
KOJ 504.0 MURADUP | Rural Long | Shire of West Arthur | 69 | 354.7 | 290.5 | 3.09 | 5.45
KOJ 504.0 MURADUP | Rural Long | Total | 294 | 294.6 | 290.5 | 2.57 | 5.45
KOJ 505.0 JINGALUP | Rural Long | Total - Shire of Kojonup | 187 | 503.2 | 290.5 | 4.48 | 5.45
KOJ 506.0 KOJONUP TOWN | Rural Short | Total - Shire of Kojonup | 726 | 199.3 | 202.5 | 4.84 | 2.09
LDE 502.0 MIRRABOOKA NORTH | Urban | Total - City of Wanneroo | 2667 | 34.2 | 123.8 | 0.13 | 1.25
LDE 503.0 HEPBURN EAST | Urban | City of Wanneroo | 3423 | 1.6 | 123.8 | 0.02 | 1.25
LDE 503.0 HEPBURN EAST | Urban | City of Swan | 457 | 0 | 123.8 | 0 | 1.25
LDE 503.0 HEPBURN EAST | Urban | Total | 3880 | 1.4 | 123.8 | 0.01 | 1.25
LDE 505.0 FURNISS RD | Urban | Total - City of Wanneroo | 698 | 0 | 123.8 | 0 | 1.25
LDE 510.0 KINGSWAY | Urban | Total - City of Wanneroo | 2680 | 0 | 123.8 | 0 | 1.25
LDE 511.0 LANDSDALE ZONE S/S 6 | Rural Short | Total - City of Wanneroo | 369 | 0 | 202.5 | 0 | 2.09
LDE 519.0 100 KINGSWAY | Urban | Total - City of Joondalup | 3553 | 111.5 | 123.8 | 0.89 | 1.25
LDE 520.0 WHITFORDS AVE | Rural Short | City of Wanneroo | 1731 | 0.5 | 202.5 | 0 | 2.09
LDE 520.0 WHITFORDS AVE | Rural Short | City of Joondalup | 888 | 46.6 | 202.5 | 0.22 | 2.09
LDE 520.0 WHITFORDS AVE | Rural Short | Total | 2619 | 16.1 | 202.5 | 0.08 | 2.09
LDE 523.0 161 HEPBURN AVE | Urban | City of Wanneroo | 1545 | 128.5 | 123.8 | 1.41 | 1.25
LDE 523.0 161 HEPBURN AVE | Urban | City of Joondalup | 1020 | 173.7 | 123.8 | 1.91 | 1.25
LDE 523.0 161 HEPBURN AVE | Urban | Total | 2565 | 146.5 | 123.8 | 1.61 | 1.25
LDE 525.0 LANDSDALE ZONE S/S 1 | Urban | City of Wanneroo | 2943 | 51.8 | 123.8 | 0.3 | 1.25
LDE 525.0 LANDSDALE ZONE S/S 1 | Urban | City of Stirling | 594 | 219.5 | 123.8 | 1.27 | 1.25
LDE 525.0 LANDSDALE ZONE S/S 1 | Urban | City of Joondalup | 220 | 777.6 | 123.8 | 4.51 | 1.25
LDE 525.0 LANDSDALE ZONE S/S 1 | Urban | Total | 3756 | 121.5 | 123.8 | 0.7 | 1.25
LDE 526.0 LANDSDALE ZONE S/S 4 | Urban | City of Swan | 1949 | 40.3 | 123.8 | 0.16 | 1.25
LDE 526.0 LANDSDALE ZONE S/S 4 | Urban | City of Wanneroo | 1708 | 2.9 | 123.8 | 0.01 | 1.25
LDE 526.0 LANDSDALE ZONE S/S 4 | Urban | Total | 3657 | 22.3 | 123.8 | 0.09 | 1.25
MA 301.0 JOYCE ST NORTH | Urban | Total - City of Stirling | 2122 | 166.1 | 123.8 | 2.24 | 1.25
MA 302.0 ANDREW | Urban | Total - City of Stirling | 4301 | 13.6 | 123.8 | 0.08 | 1.25
MA 304.0 LALOR STREET | Urban | Total - City of Stirling | 3283 | 45.4 | 123.8 | 0.65 | 1.25
MA 305.0 MANNING STREET | Urban | Total - City of Stirling | 1143 | 262.8 | 123.8 | 1.21 | 1.25
MA 307.0 JOYCE STREET SOUTH | Urban | Total - City of Stirling | 1754 | 75 | 123.8 | 0.46 | 1.25
MA 308.0 NEWBOROUGH | Urban | Total - City of Stirling | 1805 | 64.1 | 123.8 | 0.38 | 1.25
MBR 504.0 QUANGELLUP | Rural Long | Shire of Plantagenet | 2712 | 507.6 | 290.5 | 4.71 | 5.45
MBR 504.0 QUANGELLUP | Rural Long | Shire of Cranbrook | 722 | 449.3 | 290.5 | 4.17 | 5.45
MBR 504.0 QUANGELLUP | Rural Long | City of Albany | 88 | 2176.3 | 290.5 | 20.21 | 5.45
MBR 504.0 QUANGELLUP | Rural Long | Total | 3604 | 537.6 | 290.5 | 4.99 | 5.45
MBR 513.0 ROCKY GULLY | Rural Long | Shire of Plantagenet | 225 | 36.3 | 290.5 | 0.4 | 5.45
MBR 513.0 ROCKY GULLY | Rural Long | Shire of Cranbrook | 29 | 569.1 | 290.5 | 6.23 | 5.45
MBR 513.0 ROCKY GULLY | Rural Long | Shire of Manjimup | 8 | 285.7 | 290.5 | 3.13 | 5.45
MBR 513.0 ROCKY GULLY | Rural Long | Total | 263 | 103.6 | 290.5 | 1.13 | 5.45
MCE 307.0 BROADWAY FAIR | Urban | City of Perth | 796 | 42.6 | 123.8 | 0.45 | 1.25
MCE 307.0 BROADWAY FAIR | Urban | City of Nedlands | 240 | 13.9 | 123.8 | 0.15 | 1.25
MCE 307.0 BROADWAY FAIR | Urban | Total | 1036 | 35.9 | 123.8 | 0.38 | 1.25
MCE 314.0 27 ROCKTON RD RMU | Urban | City of Nedlands | 524 | 8.3 | 123.8 | 0.09 | 1.25
MCE 314.0 27 ROCKTON RD RMU | Urban | Town of Claremont | 496 | 0 | 123.8 | 0 | 1.25
MCE 314.0 27 ROCKTON RD RMU | Urban | Total | 1020 | 4.3 | 123.8 | 0.04 | 1.25
MCE 316.0 L8 PARK AVE | Rural Short | City of Perth | 373 | 0 | 202.5 | 0 | 2.09
MCE 316.0 L8 PARK AVE | Rural Short | City of Nedlands | 20 | 11.5 | 202.5 | 0.04 | 2.09
MCE 316.0 L8 PARK AVE | Rural Short | Total | 393 | 0.7 | 202.5 | 0 | 2.09
MCE 330.0 5 MONASH RMU | Urban | City of Perth | 539 | 130.3 | 123.8 | 0.23 | 1.25
MCE 330.0 5 MONASH RMU | Urban | City of Nedlands | 19 | 0 | 123.8 | 0 | 1.25
MCE 330.0 5 MONASH RMU | Urban | Total | 558 | 126 | 123.8 | 0.22 | 1.25
MCE 331.0 95 MONASH AVE | Urban | Total - City of Nedlands | 981 | 84.5 | 123.8 | 0.49 | 1.25
MCE 333.0 55 BROADWAY RMU | Urban | City of Nedlands | 685 | 12.5 | 123.8 | 0.03 | 1.25
MCE 333.0 55 BROADWAY RMU | Urban | City of Perth | 95 | 0 | 123.8 | 0 | 1.25
MCE 333.0 55 BROADWAY RMU | Urban | Total | 780 | 11 | 123.8 | 0.02 | 1.25
MCE 334.0 PARK RD | Urban | City of Nedlands | 595 | 26.2 | 123.8 | 0.27 | 1.25
MCE 334.0 PARK RD | Urban | City of Perth | 123 | 0.6 | 123.8 | 0.01 | 1.25
MCE 334.0 PARK RD | Urban | Total | 718 | 21.8 | 123.8 | 0.22 | 1.25
MCE 336.0 5 STANLEY RMU | Urban | Total - City of Nedlands | 1246 | 0.2 | 123.8 | 0 | 1.25
MDN 504.0 1828 ALBANY HWY | Urban | Total - City of Gosnells | 2228 | 28.2 | 123.8 | 0.12 | 1.25
MDN 505.0 27 ROYAL ST | Urban | Total - City of Gosnells | 2670 | 52.5 | 123.8 | 1.83 | 1.25
MDN 507.0 L138 KITSON PL | Urban | Total - City of Gosnells | 994 | 616.7 | 123.8 | 1.03 | 1.25
MDN 508.0 108 MADDINGTON RD | Rural Short | City of Gosnells | 1895 | 79.4 | 202.5 | 3.02 | 2.09
MDN 508.0 108 MADDINGTON RD | Rural Short | City of Kalamunda | 1240 | 49.1 | 202.5 | 1.87 | 2.09
MDN 508.0 108 MADDINGTON RD | Rural Short | Total | 3135 | 67.2 | 202.5 | 2.55 | 2.09
MED 504.0 L521 MCLAREN AVE | Urban | Total - City of Kwinana | 48 | 57.6 | 123.8 | 1.2 | 1.25
MED 507.0 L2 CHISHAM AVE | Urban | Total - City of Kwinana | 4516 | 200.5 | 123.8 | 2.67 | 1.25
MED 508.0 L1084 TUCKER ST | Urban | City of Kwinana | 945 | 52.5 | 123.8 | 1.09 | 1.25
MED 508.0 L1084 TUCKER ST | Urban | City of Rockingham | 29 | 43.8 | 123.8 | 0.91 | 1.25
MED 508.0 L1084 TUCKER ST | Urban | Total | 974 | 52.2 | 123.8 | 1.08 | 1.25
MED 511.0 16 ABERCROMBIE RD | Rural Short | Total - City of Kwinana | 3068 | 172.6 | 202.5 | 4.18 | 2.09
MED 513.0 L1047 BROWNELL CRES | Rural Short | City of Kwinana | 2793 | 260.1 | 202.5 | 3.35 | 2.09
MED 513.0 L1047 BROWNELL CRES | Rural Short | City of Rockingham | 172 | 229.1 | 202.5 | 2.95 | 2.09
MED 513.0 L1047 BROWNELL CRES | Rural Short | Total | 2965 | 258.5 | 202.5 | 3.33 | 2.09
MED 517.0 L1084 TUCKER ST | Urban | Total - City of Kwinana | 21 | 74 | 123.8 | 1.82 | 1.25
MED 522.0 ABERCROMBIE RD SOUTH | Rural Short | Total - City of Kwinana | 1979 | 431.4 | 202.5 | 6.19 | 2.09
MED 524.0 MEDINA S/S RMU | Rural Short | City of Kwinana | 3579 | 237.6 | 202.5 | 2.92 | 2.09
MED 524.0 MEDINA S/S RMU | Rural Short | City of Rockingham | 595 | 74.3 | 202.5 | 0.91 | 2.09
MED 524.0 MEDINA S/S RMU | Rural Short | Total | 4202 | 214.9 | 202.5 | 2.64 | 2.09
MED 526.0 ABERCROMBIE RD NORTH | Rural Short | City of Kwinana | 2188 | 115.2 | 202.5 | 3.27 | 2.09
MED 526.0 ABERCROMBIE RD NORTH | Rural Short | Shire of Serpentine-Jarrahdale | 102 | 304.7 | 202.5 | 8.64 | 2.09
MED 526.0 ABERCROMBIE RD NORTH | Rural Short | City of Cockburn | 92 | 14 | 202.5 | 0.4 | 2.09
MED 526.0 ABERCROMBIE RD NORTH | Rural Short | Total | 2382 | 99.4 | 202.5 | 2.82 | 2.09
MER 506.0 MERREDIN | Rural Short | Total - Shire of Merredin | 1323 | 463.5 | 202.5 | 4.29 | 2.09
MER 507.0 BURRACOPPIN | Rural Long | Shire of Merredin | 396 | 296.5 | 290.5 | 1.84 | 5.45
MER 507.0 BURRACOPPIN | Rural Long | Shire of Westonia | 18 | 756.2 | 290.5 | 4.69 | 5.45
MER 507.0 BURRACOPPIN | Rural Long | Total | 418 | 317 | 290.5 | 1.97 | 5.45
MER 515.0 BRUCE ROCK TOWN | Rural Long | Shire of Bruce Rock | 540 | 428.8 | 290.5 | 3.39 | 5.45
MER 515.0 BRUCE ROCK TOWN | Rural Long | Shire of Merredin | 114 | 952.9 | 290.5 | 7.54 | 5.45
MER 515.0 BRUCE ROCK TOWN | Rural Long | Shire of Narembeen | 25 | 893.5 | 290.5 | 7.07 | 5.45
MER 515.0 BRUCE ROCK TOWN | Rural Long | Total | 679 | 533.8 | 290.5 | 4.22 | 5.45
MER 516.0 NUNGARIN | Rural Long | Shire of Mount Marshall | 449 | 2524.8 | 290.5 | 17.95 | 5.45
MER 516.0 NUNGARIN | Rural Long | Shire of Mukinbudin | 407 | 3071.5 | 290.5 | 21.84 | 5.45
MER 516.0 NUNGARIN | Rural Long | Shire of Nungarin | 139 | 1129.5 | 290.5 | 8.03 | 5.45
MER 516.0 NUNGARIN | Rural Long | Shire of Merredin | 129 | 1024.1 | 290.5 | 7.28 | 5.45
MER 516.0 NUNGARIN | Rural Long | Total | 1147 | 2379 | 290.5 | 16.92 | 5.45
MH 501.0 CLARICE ST (F)/106 WATERSI | Urban | Total - City of Mandurah | 3736 | 42.7 | 123.8 | 0.38 | 1.25
MH 502.0 ELIZABETH | Urban | Total - City of Mandurah | 4094 | 29.1 | 123.8 | 1.04 | 1.25
MH 504.0 FRANCE | Urban | Total - City of Mandurah | 3237 | 1.7 | 123.8 | 0.03 | 1.25
MH 509.0 WAXFLOWER VSTA | Urban | Total - City of Mandurah | 4300 | 616.8 | 123.8 | 7.22 | 1.25
MH 512.0 LANYON | Rural Short | Total - City of Mandurah | 4313 | 344.2 | 202.5 | 3.41 | 2.09
MH 515.0 CLARICE | Urban | City of Mandurah | 596 | 135.1 | 123.8 | 2.11 | 1.25
MH 515.0 CLARICE | Urban | Shire of Murray | 208 | 56.6 | 123.8 | 0.88 | 1.25
MH 515.0 CLARICE | Urban | Total | 804 | 99 | 123.8 | 1.54 | 1.25
MH 520.0 DOWER.S | Rural Short | City of Mandurah | 1910 | 118.4 | 202.5 | 2.14 | 2.09
MH 520.0 DOWER.S | Rural Short | Shire of Murray | 294 | 210.8 | 202.5 | 3.81 | 2.09
MH 520.0 DOWER.S | Rural Short | Total | 2204 | 164 | 202.5 | 2.97 | 2.09
MH 521.0 OLD COAST RD | Urban | Total - City of Mandurah | 4235 | 444.4 | 123.8 | 8.08 | 1.25
MH 522.0 79 ALLNUTT ST | Urban | Total - City of Mandurah | 4339 | 45 | 123.8 | 0.29 | 1.25
MIL 301.0 778 HAY ST (TOWN HOUSE) | CBD | Total - City of Perth | 59 | 0 | 13.7 | 0 | 0.21
MIL 303.0 441 MURRAY/214 ST GEO TCE | CBD | Total - City of Perth | 267 | 0 | 13.7 | 0 | 0.21
MIL 307.0 5 MILL ST/942 HAY ST | CBD | Total - City of Perth | 218 | 69 | 13.7 | 1.43 | 0.21
MIL 309.0 170 ST.GEO.TCE/DAILY NEWS | CBD | City of Perth | 584 | 17.5 | 13.7 | 0.01 | 0.21
MIL 309.0 170 ST.GEO.TCE/DAILY NEWS | CBD | City of Vincent | 50 | 2.5 | 13.7 | 0 | 0.21
MIL 309.0 170 ST.GEO.TCE/DAILY NEWS | CBD | Total | 634 | 16.3 | 13.7 | 0.01 | 0.21
MIL 312.0 918HAY/560WELLINGTON ST | CBD | Total - City of Perth | 267 | 4.6 | 13.7 | 1.06 | 0.21
MIL 314.0 108.ST.GEO.TCE | CBD | Total - City of Perth | 38 | 0 | 13.7 | 0 | 0.21
MIL 316.0 14 SPRING ST/CUSTOM | CBD | Total - City of Perth | 75 | 0 | 13.7 | 0 | 0.21
MIL 319.0 468 MURRAY/14 SPRING ST 2 | CBD | Total - City of Perth | 211 | 196.4 | 13.7 | 0.54 | 0.21
MIL 327.0 | CBD | Total - City of Perth | 192 | 0 | 13.7 | 0 | 0.21
MIL 330.0 976 HAY ST (QVI CARPARK) | CBD | Total - City of Perth | 125 | 25.7 | 13.7 | 0.03 | 0.21
MIL 332.0 160 ST.GEO.TCE | CBD | Total - City of Perth | 12 | 0 | 13.7 | 0 | 0.21
MIL 337.0 996 HAY ST | CBD | Total - City of Perth | 48 | 0 | 13.7 | 0 | 0.21
MIL 339.0 14 LAKE ST/220 ST GEO | CBD | Total - City of Perth | 172 | 84.4 | 13.7 | 1.5 | 0.21
MIL 345.0 200 ST GEO T/556 WELLINGT | CBD | Total - City of Perth | 20 | 0 | 13.7 | 0 | 0.21
MIL 348.0 33 MALCOLM ST | CBD | Total - City of Perth | 562 | 0 | 13.7 | 0 | 0.21
MIL 350.0 ENTERTAIN/CEN /185 ST GEO | CBD | Total - City of Perth | 71 | 0 | 13.7 | 0 | 0.21
MIL 352.0 88 COLIN ST.503 MURRAY ST | CBD | Total - City of Perth | 13 | 0 | 13.7 | 0 | 0.21
MIL 354.0 1 THE ESPLANANDE | CBD | Total - City of Perth | 157 | 53.2 | 13.7 | 1 | 0.21
MJ 503.0 BRICKWORKS #2 | Urban | Total - City of Swan | 1884 | 214.2 | 123.8 | 0.65 | 1.25
MJ 504.0 LLOYD ST/9 BROCKMAN RD | Urban | Total - City of Swan | 1264 | 55.4 | 123.8 | 1.09 | 1.25
MJ 506.0 THE CRESCENT ROUNDABOUT | Urban | Total - City of Swan | 1972 | 87.3 | 123.8 | 0.23 | 1.25
MJ 508.0 GREENMOUNT/CADCOM ZONE 2 | Urban | Shire of Mundaring | 2089 | 26.5 | 123.8 | 0.73 | 1.25
MJ 508.0 GREENMOUNT/CADCOM ZONE 2 | Urban | City of Swan | 1434 | 91.6 | 123.8 | 2.5 | 1.25
MJ 508.0 GREENMOUNT/CADCOM ZONE 2 | Urban | Total | 3523 | 53 | 123.8 | 1.45 | 1.25
MJ 510.0 SWANVIEW | Rural Short | City of Swan | 3486 | 198.2 | 202.5 | 4.33 | 2.09
MJ 510.0 SWANVIEW | Rural Short | Shire of Mundaring | 358 | 258.8 | 202.5 | 5.65 | 2.09
MJ 510.0 SWANVIEW | Rural Short | Total | 3844 | 203.4 | 202.5 | 4.44 | 2.09
MJ 514.0 BUSHMEAD/MIDLAND GATE | Urban | City of Swan | 725 | 40 | 123.8 | 0.24 | 1.25
MJ 514.0 BUSHMEAD/MIDLAND GATE | Urban | Shire of Mundaring | 233 | 74.9 | 123.8 | 0.44 | 1.25
MJ 514.0 BUSHMEAD/MIDLAND GATE | Urban | Total | 958 | 48.6 | 123.8 | 0.29 | 1.25
MJ 515.0 28 HYDE ST | Urban | Total - City of Swan | 12 | 0 | 123.8 | 0 | 1.25
MJ 528.0 BRICK WORKS NO1 | Urban | Total - City of Swan | 845 | 52.5 | 123.8 | 0.48 | 1.25
MJ 537.0 19 ABINGDON RD | Rural Short | City of Swan | 1976 | 124.7 | 202.5 | 1.01 | 2.09
MJ 537.0 19 ABINGDON RD | Rural Short | Shire of Mundaring | 1259 | 243.3 | 202.5 | 1.97 | 2.09
MJ 537.0 19 ABINGDON RD | Rural Short | Total | 3235 | 177.2 | 202.5 | 1.43 | 2.09
MJ 538.0 16 JAMES RD | Rural Short | Total - City of Swan | 926 | 608.8 | 202.5 | 8.31 | 2.09
MJP 507.0 PEMBERTON | Rural Long | Total - Shire of Manjimup | 915 | 647.4 | 290.5 | 3.36 | 5.45
MJP 511.0 MANJIMUP | Rural Short | Total - Shire of Manjimup | 1692 | 268.1 | 202.5 | 1.24 | 2.09
MJP 512.0 DEANMILL | Rural Long | Total - Shire of Manjimup | 1793 | 295.9 | 290.5 | 3.44 | 5.45
MJP 514.0 QUINNINUP | Rural Long | Total - Shire of Manjimup | 815 | 471.6 | 290.5 | 1.81 | 5.45
MLG 510.0 BEACH RD | Urban | City of Stirling | 1404 | 28.7 | 123.8 | 0.12 | 1.25
MLG 510.0 BEACH RD | Urban | City of Swan | 412 | 5.4 | 123.8 | 0.02 | 1.25
MLG 510.0 BEACH RD | Urban | Total | 1816 | 23.3 | 123.8 | 0.1 | 1.25
MLG 524.0 33 HOLDER ST | Urban | Total - City of Swan | 701 | 36.8 | 123.8 | 0.13 | 1.25
MLG 527.0 12 WIDGE RD | Urban | City of Stirling | 1722 | 33.9 | 123.8 | 0.16 | 1.25
MLG 527.0 12 WIDGE RD | Urban | City of Bayswater | 616 | 27.9 | 123.8 | 0.13 | 1.25
MLG 527.0 12 WIDGE RD | Urban | Total | 2338 | 32.3 | 123.8 | 0.15 | 1.25
MLG 543.0 | Urban | City of Stirling | 1383 | 44.4 | 123.8 | 0.92 | 1.25
MLG 543.0 | Urban | City of Wanneroo | 1256 | 31.3 | 123.8 | 0.64 | 1.25
MLG 543.0 | Urban | City of Swan | 696 | 97.1 | 123.8 | 2 | 1.25
MLG 543.0 | Urban | Total | 3335 | 46.1 | 123.8 | 0.95 | 1.25
MLG 546.0 25 FINANCE PL | Urban | Total - City of Swan | 2139 | 28.6 | 123.8 | 0.08 | 1.25
MLG 547.0 | Urban | Total - City of Swan | 2884 | 10.7 | 123.8 | 0.03 | 1.25
MO 337.0 LAWRENCE ST | Urban | City of Bayswater | 2540 | 86.8 | 123.8 | 1.35 | 1.25
MO 337.0 LAWRENCE ST | Urban | City of Stirling | 1270 | 94.8 | 123.8 | 1.47 | 1.25
MO 337.0 LAWRENCE ST | Urban | Total | 3810 | 89.5 | 123.8 | 1.39 | 1.25
MO 338.0 | Urban | City of Bayswater | 3149 | 46.2 | 123.8 | 0.77 | 1.25
MO 338.0 | Urban | City of Stirling | 636 | 11.5 | 123.8 | 0.19 | 1.25
MO 338.0 | Urban | Total | 3785 | 41.2 | 123.8 | 0.69 | 1.25
MO 340.0 L47 CATHERINE ST | Urban | Total - City of Bayswater | 2057 | 81.7 | 123.8 | 0.93 | 1.25
MO 341.0 CATHERINE ST | Urban | City of Stirling | 976 | 46.3 | 123.8 | 0.25 | 1.25
MO 341.0 CATHERINE ST | Urban | City of Bayswater | 451 | 63.7 | 123.8 | 0.34 | 1.25
MO 341.0 CATHERINE ST | Urban | Total | 1427 | 51.7 | 123.8 | 0.27 | 1.25
MO 354.0 145 RUSSELL ST | Urban | City of Stirling | 1344 | 158.6 | 123.8 | 3.9 | 1.25
MO 354.0 145 RUSSELL ST | Urban | City of Bayswater | 394 | 0 | 123.8 | 0 | 1.25
MO 354.0 145 RUSSELL ST | Urban | Total | 1738 | 122.6 | 123.8 | 3.02 | 1.25
MO 355.0 231 DRAKE ST | Urban | City of Bayswater | 670 | 38.8 | 123.8 | 0.39 | 1.25
MO 355.0 231 DRAKE ST | Urban | City of Stirling | 566 | 82.8 | 123.8 | 0.83 | 1.25
MO 355.0 231 DRAKE ST | Urban | Total | 1236 | 58.9 | 123.8 | 0.59 | 1.25
MO 357.0 R.A COOK RESERVE B | Urban | Total - City of Stirling | 1399 | 39.4 | 123.8 | 0.07 | 1.25
MO 361.0 GOODE ST EAST | Urban | Total - City of Bayswater | 1983 | 104 | 123.8 | 0.53 | 1.25
MO 362.0 FORT ST | Urban | Total - City of Bayswater | 1496 | 70.6 | 123.8 | 0.39 | 1.25
MO 370.0 GOODE ST WEST | Urban | City of Stirling | 1564 | 93.4 | 123.8 | 0.62 | 1.25
MO 370.0 GOODE ST WEST | Urban | City of Bayswater | 358 | 126.9 | 123.8 | 0.84 | 1.25
MO 370.0 GOODE ST WEST | Urban | Total | 1922 | 99.5 | 123.8 | 0.66 | 1.25
MO 371.0 RUSSELL ST | Urban | Total - City of Bayswater | 122 | 4.6 | 123.8 | 0.02 | 1.25
MOR 601.0 MOORA | Rural Short | Total - Shire of Moora | 936 | 54.2 | 202.5 | 2.13 | 2.09
MOR 603.0 NEW NORCIA | Rural Long | Shire of Victoria Plains | 451 | 2029.4 | 290.5 | 12.61 | 5.45
MOR 603.0 NEW NORCIA | Rural Long | Shire of Moora | 39 | 1533.2 | 290.5 | 9.52 | 5.45
MOR 603.0 NEW NORCIA | Rural Long | Shire of Goomalling | 16 | 1350 | 290.5 | 8.39 | 5.45
MOR 603.0 NEW NORCIA | Rural Long | Shire of Dandaragan | 12 | 317.1 | 290.5 | 1.97 | 5.45
MOR 603.0 NEW NORCIA | Rural Long | Total | 520 | 1929.5 | 290.5 | 11.99 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Shire of Wongan-Ballidu | 949 | 1548.9 | 290.5 | 9.19 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Shire of Dalwallinu | 176 | 2954.5 | 290.5 | 17.53 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Shire of Goomalling | 61 | 2358 | 290.5 | 13.99 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Shire of Dowerin | 60 | 2732.8 | 290.5 | 16.22 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Shire of Koorda | 45 | 3128.3 | 290.5 | 18.57 | 5.45
MOR 607.0 WONGAN HILLS SOUTH | Rural Long | Total | 1300 | 1887.8 | 290.5 | 11.2 | 5.45
MOR 609.0 WONGAN HILLS NORTH | Rural Long | Shire of Moora | 101 | 3447 | 290.5 | 2.84 | 5.45
MOR 609.0 WONGAN HILLS NORTH | Rural Long | Shire of Wongan-Ballidu | 34 | 8816.2 | 290.5 | 7.26 | 5.45
MOR 609.0 WONGAN HILLS NORTH | Rural Long | Shire of Victoria Plains | 19 | 9522.7 | 290.5 | 7.85 | 5.45
MOR 609.0 WONGAN HILLS NORTH | Rural Long | Total | 155 | 5433.3 | 290.5 | 4.48 | 5.45
MOR 610.0 DALWALLINU | Rural Long | Shire of Dalwallinu | 770 | 3100.8 | 290.5 | 13.5 | 5.45
MOR 610.0 DALWALLINU | Rural Long | Shire of Moora | 128 | 2788.5 | 290.5 | 12.14 | 5.45
MOR 610.0 DALWALLINU | Rural Long | Total | 900 | 3056.4 | 290.5 | 13.31 | 5.45
MOR 612.0 WATHEROO | Rural Long | Shire of Moora | 213 | 1960.5 | 290.5 | 5.52 | 5.45
MOR 612.0 WATHEROO | Rural Long | Shire of Coorow | 70 | 2711.6 | 290.5 | 7.64 | 5.45
MOR 612.0 WATHEROO | Rural Long | Shire of Dalwallinu | 13 | 6522.7 | 290.5 | 18.37 | 5.45
MOR 612.0 WATHEROO | Rural Long | Shire of Dandaragan | 7 | 1681 | 290.5 | 4.74 | 5.45
MOR 612.0 WATHEROO | Rural Long | Total | 302 | 2315.5 | 290.5 | 6.52 | 5.45
MOR 613.0 DANDARAGAN | Rural Long | Shire of Dandaragan | 616 | 1642.7 | 290.5 | 5.54 | 5.45
MOR 613.0 DANDARAGAN | Rural Long | Shire of Moora | 83 | 365.4 | 290.5 | 1.23 | 5.45
MOR 613.0 DANDARAGAN | Rural Long | Total | 699 | 1488.5 | 290.5 | 5.02 | 5.45
MR 508.0 AUGUSTA | Rural Long | Total - Shire of Augusta-Margaret River | 2586 | 153.1 | 290.5 | 2.31 | 5.45
MR 550.0 COWARAMUP | Rural Long | Shire of Augusta-Margaret River | 2201 | 106.3 | 290.5 | 2.89 | 5.45
MR 550.0 COWARAMUP | Rural Long | City of Busselton | 111 | 417.8 | 290.5 | 11.36 | 5.45
MR 550.0 COWARAMUP | Rural Long | Total | 2312 | 121.5 | 290.5 | 3.3 | 5.45
MR 551.0 PREVELLY | Rural Short | Total - Shire of Augusta-Margaret River | 3139 | 190.2 | 202.5 | 2.92 | 2.09
MRR 502.0 DEVLIN RD | Rural Short | Total - Shire of Harvey | 3314 | 59.1 | 202.5 | 1.03 | 2.09
MRR 503.0 MARRIOT ROAD EAST | Rural Short | Total - Shire of Harvey | 1642 | 1238.7 | 202.5 | 5.22 | 2.09
MRR 531.0 MARRIOT ROAD EAST | Rural Long | Total - Shire of Harvey | 106 | 0.8 | 290.5 | 0.01 | 5.45
MRR 534.0 BINNINGUP | Rural Long | Total - Shire of Harvey | 1464 | 787 | 290.5 | 3.33 | 5.45
MSR 506.0 PATTERSON RD | Urban | City of Kwinana | 35 | 203.7 | 123.8 | 2.14 | 1.25
MSR 506.0 PATTERSON RD | Urban | City of Rockingham | 6 | 303.3 | 123.8 | 3.19 | 1.25
MSR 506.0 PATTERSON RD | Urban | Total | 41 | 220.6 | 123.8 | 2.32 | 1.25
MSR 507.0 MANDURAH RD | Urban | Total - City of Kwinana | 146 | 179 | 123.8 | 2.15 | 1.25
MSS 504.0 L1808 TANDURE CIR | Rural Short | City of Mandurah | 3599 | 408.4 | 202.5 | 2.77 | 2.09
MSS 504.0 L1808 TANDURE CIR | Rural Short | Shire of Murray | 170 | 508.5 | 202.5 | 3.45 | 2.09
MSS 504.0 L1808 TANDURE CIR | Rural Short | Total | 3769 | 413 | 202.5 | 2.8 | 2.09
MSS 505.0 L327 FREMANTLE RD | Urban | City of Rockingham | 2463 | 217.1 | 123.8 | 2.74 | 1.25
MSS 505.0 L327 FREMANTLE RD | Urban | City of Mandurah | 450 | 38.2 | 123.8 | 0.48 | 1.25
MSS 505.0 L327 FREMANTLE RD | Urban | Total | 2913 | 162.6 | 123.8 | 2.05 | 1.25
MSS 508.0 MEADOW SPRINGS B RMU | Urban | Total - City of Mandurah | 4785 | 12.3 | 123.8 | 0.08 | 1.25
MSS 529.0 PARKLANDS TUNNEL | Rural Short | City of Rockingham | 3614 | 276.7 | 202.5 | 2.96 | 2.09
MSS 529.0 PARKLANDS TUNNEL | Rural Short | City of Mandurah | 390 | 157 | 202.5 | 1.68 | 2.09
MSS 529.0 PARKLANDS TUNNEL | Rural Short | Total | 4032 | 265.2 | 202.5 | 2.83 | 2.09
MSS 530.0 L281 GORDON RD | Urban | Total - City of Mandurah | 4303 | 136.3 | 123.8 | 2.79 | 1.25
MSS 536.0 L9003 MANDURAH RD | Urban | City of Rockingham | 3718 | 73.4 | 123.8 | 1.77 | 1.25
MSS 536.0 L9003 MANDURAH RD | Urban | City of Mandurah | 339 | 128.1 | 123.8 | 3.08 | 1.25
MSS 536.0 L9003 MANDURAH RD | Urban | Total | 4057 | 77.3 | 123.8 | 1.86 | 1.25
MSS 540.0 L303 MEADOW SPRINGS DRV | Urban | Total - City of Mandurah | 4138 | 99.1 | 123.8 | 0.34 | 1.25
MUC 505.0 FEWSTER STH | Rural Short | City of Swan | 903 | 1084.5 | 202.5 | 5.84 | 2.09
MUC 505.0 FEWSTER STH | Rural Short | Shire of Chittering | 235 | 781.7 | 202.5 | 4.21 | 2.09
MUC 505.0 FEWSTER STH | Rural Short | Total | 1138 | 1028.9 | 202.5 | 5.54 | 2.09
MUC 510.0 GREAT NORTHERN HWY | Rural Long | Total - Shire of Chittering | 2305 | 567.1 | 290.5 | 6.89 | 5.45
MUC 511.0 BRAND NTH | Rural Short | City of Wanneroo | 33 | 106.2 | 202.5 | 0.52 | 2.09
MUC 511.0 BRAND NTH | Rural Short | Shire of Chittering | 3 | 1254.3 | 202.5 | 6.17 | 2.09
MUC 511.0 BRAND NTH | Rural Short | Total | 36 | 202.8 | 202.5 | 1 | 2.09
MUC 536.0 BRAND SOUTH (LS) | Rural Short | City of Swan | 2131 | 99.9 | 202.5 | 1.64 | 2.09
MUC 536.0 BRAND SOUTH (LS) | Rural Short | Shire of Chittering | 155 | 67.7 | 202.5 | 1.11 | 2.09
MUC 536.0 BRAND SOUTH (LS) | Rural Short | Total | 2286 | 97.6 | 202.5 | 1.61 | 2.09
MUC 537.0 L1702 BRYNE RD | Rural Long | Shire of Gingin | 984 | 1437.3 | 290.5 | 6.48 | 5.45
MUC 537.0 L1702 BRYNE RD | Rural Long | Shire of Chittering | 48 | 201.3 | 290.5 | 0.91 | 5.45
MUC 537.0 L1702 BRYNE RD | Rural Long | Total | 1032 | 1378.6 | 290.5 | 6.21 | 5.45
MUL 503.0 OCEAN REEF RD | Urban | Total - City of Joondalup | 3390 | 94 | 123.8 | 0.36 | 1.25
MUL 504.0 BEENYUP TREATMENT PLANT | Urban | Total - City of Joondalup | 975 | 405.5 | 123.8 | 4.07 | 1.25
MUL 507.0 WANGARA | Rural Short | Total - City of Wanneroo | 1880 | 197 | 202.5 | 2.13 | 2.09
MUL 509.0 MULLALOO DRIVE EAST | Urban | City of Wanneroo | 2689 | 87.5 | 123.8 | 1.02 | 1.25
MUL 509.0 MULLALOO DRIVE EAST | Urban | City of Joondalup | 584 | 107.1 | 123.8 | 1.25 | 1.25
MUL 509.0 MULLALOO DRIVE EAST | Urban | Total | 3273 | 90.9 | 123.8 | 1.06 | 1.25
MUL 510.0 JOONDALUP DRIVE | Urban | Total - City of Joondalup | 420 | 54.2 | 123.8 | 0.2 | 1.25
MUL 515.0 L11 JOONDALUP DR RMU | Urban | Total - City of Joondalup | 1168 | 205.9 | 123.8 | 1.5 | 1.25
MUL 518.0 TRAPPERS/CONIDAE | Urban | Total - City of Joondalup | 3629 | 73.7 | 123.8 | 0.38 | 1.25
MUL 520.0 WEDGEWOOD | Urban | Total - City of Joondalup | 820 | 74.7 | 123.8 | 1.12 | 1.25
MUL 522.0 49 JOONDALUP DR | Urban | Total - City of Joondalup | 45 | 0 | 123.8 | 0 | 1.25
MUR 504.0 L4252 MURDOCH DR | Urban | City of Melville | 412 | 51.4 | 123.8 | 2.13 | 1.25
MUR 504.0 L4252 MURDOCH DR | Urban | City of Cockburn | 206 | 44.6 | 123.8 | 1.85 | 1.25
MUR 504.0 L4252 MURDOCH DR | Urban | Total | 618 | 49.1 | 123.8 | 2.04 | 1.25
MUR 507.0 125 CASSERLEY AVE | Urban | City of Cockburn | 1145 | 338.4 | 123.8 | 0.24 | 1.25
MUR 507.0 125 CASSERLEY AVE | Urban | City of Melville | 368 | 0 | 123.8 | 0 | 1.25
MUR 507.0 125 CASSERLEY AVE | Urban | Total | 1513 | 256.5 | 123.8 | 0.18 | 1.25
MUR 524.0 HOPE RD | Rural Short | Total - City of Cockburn | 2349 | 190.6 | 202.5 | 2.15 | 2.09
MUR 525.0 MURDOCH STATION | Urban | City of Melville | 9 | 0 | 123.8 | 0 | 1.25
MUR 525.0 MURDOCH STATION | Urban | City of Cockburn | 2 | 0 | 123.8 | 0 | 1.25
MUR 525.0 MURDOCH STATION | Urban | Total | 11 | 0 | 123.8 | 0 | 1.25
MUR 527.0 MURDOCH DR 1 RMU | Urban | Total - City of Melville | 1545 | 271.3 | 123.8 | 3.15 | 1.25
MYR 501.0 GARDEN CITY SW/RM | Urban | Total - City of Melville | 253 | 0 | 123.8 | 0 | 1.25
MYR 504.0 709 CANNING HWY | Urban | Total - City of Melville | 1728 | 5.3 | 123.8 | 0.09 | 1.25
MYR 505.0 OPP 185 KITCHENER RD | Urban | Total - City of Melville | 3016 | 14.2 | 123.8 | 0.05 | 1.25
MYR 508.0 NORMA RD NORTH | Urban | Total - City of Melville | 2016 | 7.7 | 123.8 | 0.09 | 1.25
MYR 510.0 KITCHENER RD EAST | Urban | Total - City of Melville | 2065 | 34.1 | 123.8 | 1.83 | 1.25
MYR 511.0 20 HORROCKS RD | Urban | Total - City of Melville | 2307 | 13.9 | 123.8 | 0.04 | 1.25
MYR 514.0 NORMA RD SOUTH | Urban | Total - City of Melville | 85 | 210.7 | 123.8 | 1.01 | 1.25
NB 501.0 37 EVERINGHAM ST | Urban | City of Joondalup | 1681 | 48.2 | 123.8 | 0.88 | 1.25
NB 501.0 37 EVERINGHAM ST | Urban | City of Stirling | 603 | 0 | 123.8 | 0 | 1.25
NB 501.0 37 EVERINGHAM ST | Urban | Total | 2284 | 36.8 | 123.8 | 0.67 | 1.25
NB 502.0 WALDORF ST | Urban | City of Stirling | 1347 | 388.6 | 123.8 | 2.38 | 1.25
NB 502.0 WALDORF ST | Urban | City of Joondalup | 368 | 366.3 | 123.8 | 2.25 | 1.25
NB 502.0 WALDORF ST | Urban | Total | 1715 | 384.8 | 123.8 | 2.36 | 1.25
NB 504.0 BRADWELL ST | Urban | Total - City of Stirling | 2473 | 38.4 | 123.8 | 0.76 | 1.25
NB 508.0 CLEMENT DR | Urban | Total - City of Stirling | 1908 | 636.4 | 123.8 | 3.46 | 1.25
NB 513.0 MARMION AVE | Rural Short | City of Joondalup | 1363 | 169 | 202.5 | 1.29 | 2.09
NB 513.0 MARMION AVE | Rural Short | City of Stirling | 110 | 106.4 | 202.5 | 0.81 | 2.09
NB 513.0 MARMION AVE | Rural Short | Total | 1473 | 164.3 | 202.5 | 1.25 | 2.09
NB 514.0 REID HWY | Urban | City of Joondalup | 1532 | 31.3 | 123.8 | 0.26 | 1.25
NB 514.0 REID HWY | Urban | City of Stirling | 431 | 0 | 123.8 | 0 | 1.25
NB 514.0 REID HWY | Urban | Total | 1963 | 24.4 | 123.8 | 0.2 | 1.25
NB 518.0 EVERINGHAM ST NORTH | Urban | City of Joondalup | 1530 | 106.8 | 123.8 | 1.03 | 1.25
NB 518.0 EVERINGHAM ST NORTH | Urban | City of Stirling | 438 | 265.2 | 123.8 | 2.55 | 1.25
NB 518.0 EVERINGHAM ST NORTH | Urban | Total | 1968 | 142.2 | 123.8 | 1.37 | 1.25
NB 519.0 BEACH RD WEST | Urban | City of Joondalup | 2046 | 288.4 | 123.8 | 2.9 | 1.25
NB 519.0 BEACH RD WEST | Urban | City of Stirling | 1085 | 232.6 | 123.8 | 2.34 | 1.25
NB 519.0 BEACH RD WEST | Urban | Total | 3131 | 269.1 | 123.8 | 2.71 | 1.25
NB 520.0 EVERINGHAM ST STH | Urban | Total - City of Stirling | 487 | 847.9 | 123.8 | 2.09 | 1.25
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Pingelly | 724 | 596.1 | 290.5 | 3.75 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Narrogin | 702 | 240.3 | 290.5 | 1.51 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Brookton | 603 | 1239 | 290.5 | 7.79 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Beverley | 138 | 2016.1 | 290.5 | 12.67 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Cuballing | 77 | 576 | 290.5 | 3.62 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Shire of Corrigin | 46 | 1557.1 | 290.5 | 9.79 | 5.45
NGN 502.0 NARROGIN EAST | Rural Long | Total | 2289 | 761 | 290.5 | 4.78 | 5.45
NGN 504.0 NARROGIN WEST | Rural Short | Total - Shire of Narrogin | 1655 | 511.4 | 202.5 | 10.7 | 2.09
NGN 506.0 WILLIAMS | Rural Long | Shire of Williams | 563 | 99.5 | 290.5 | 0.44 | 5.45
NGN 506.0 WILLIAMS | Rural Long | Shire of Narrogin | 147 | 137.6 | 290.5 | 0.61 | 5.45
NGN 506.0 WILLIAMS | Rural Long | Shire of Boddington | 39 | 206.5 | 290.5 | 0.92 | 5.45
NGN 506.0 WILLIAMS | Rural Long | Total | 750 | 112.9 | 290.5 | 0.5 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Shire of Narrogin | 194 | 370.4 | 290.5 | 1.11 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Shire of Wickepin | 102 | 1056.4 | 290.5 | 3.15 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Shire of Kulin | 27 | 262.6 | 290.5 | 0.78 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Shire of Wagin | 25 | 471.9 | 290.5 | 1.41 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Shire of Dumbleyung | 18 | 657.4 | 290.5 | 1.96 | 5.45
NGN 509.0 HIGHBURY | Rural Long | Total | 366 | 573.8 | 290.5 | 1.71 | 5.45
NGN 511.0 WICKEPIN | Rural Long | Shire of Narrogin | 90 | 1918.6 | 290.5 | 9.27 | 5.45
NGN 511.0 WICKEPIN | Rural Long | Shire of Cuballing | 41 | 2368.3 | 290.5 | 11.45 | 5.45
NGN 511.0 WICKEPIN | Rural Long | Shire of Wickepin | 9 | 154.8 | 290.5 | 0.75 | 5.45
NGN 511.0 WICKEPIN | Rural Long | Total | 141 | 872.2 | 290.5 | 4.22 | 5.45
NGN 513.0 BROOKTON | Rural Long | Shire of Cuballing | 404 | 214.2 | 290.5 | 1.08 | 5.45
NGN 513.0 BROOKTON | Rural Long | Shire of Wandering | 232 | 364.8 | 290.5 | 1.85 | 5.45
NGN 513.0 BROOKTON | Rural Long | Shire of Pingelly | 23 | 868.1 | 290.5 | 4.39 | 5.45
NGN 513.0 BROOKTON | Rural Long | Shire of Narrogin | 21 | 82.1 | 290.5 | 0.42 | 5.45
NGN 513.0 BROOKTON | Rural Long | Total | 702 | 283.1 | 290.5 | 1.43 | 5.45
NOR 501.0 GRASS VALLEY | Urban | Total - Shire of Northam | 30 | 245.8 | 123.8 | 1.75 | 1.25
NOR 502.0 GOOMALLING | Rural Long | Shire of Goomalling | 572 | 1479.2 | 290.5 | 5.62 | 5.45
NOR 502.0 GOOMALLING | Rural Long | Shire of Northam | 187 | 657.8 | 290.5 | 2.5 | 5.45
NOR 502.0 GOOMALLING | Rural Long | Total | 772 | 1278.6 | 290.5 | 4.86 | 5.45
NOR 512.0 NORTHAM SOUTH | Rural Short | Total - Shire of Northam | 874 | 409.3 | 202.5 | 6.1 | 2.09
NOR 532.0 TOODYAY EAST | Rural Long | Shire of Toodyay | 1727 | 666.3 | 290.5 | 5.91 | 5.45
NOR 532.0 TOODYAY EAST | Rural Long | Shire of Victoria Plains | 126 | 346.5 | 290.5 | 3.07 | 5.45
NOR 532.0 TOODYAY EAST | Rural Long | Total | 1863 | 644.6 | 290.5 | 5.72 | 5.45
NOR 535.0 TOODYAY WEST | Rural Short | Shire of Toodyay | 669 | 301.7 | 202.5 | 2.42 | 2.09
NOR 535.0 TOODYAY WEST | Rural Short | Shire of Northam | 273 | 273.7 | 202.5 | 2.2 | 2.09
NOR 535.0 TOODYAY WEST | Rural Short | Total | 942 | 293.7 | 202.5 | 2.36 | 2.09
NOR 538.0 NORTHAM NORTH | Rural Short | Total - Shire of Northam | 1323 | 64.4 | 202.5 | 1.4 | 2.09
NOR 540.0 YORK | Rural Long | Shire of York | 2185 | 495.4 | 290.5 | 6.15 | 5.45
NOR 540.0 YORK | Rural Long | Shire of Beverley | 990 | 1212.9 | 290.5 | 15.05 | 5.45
NOR 540.0 YORK | Rural Long | Shire of Northam | 153 | 157.5 | 290.5 | 1.95 | 5.45
NOR 540.0 YORK | Rural Long | Total | 3332 | 694.3 | 290.5 | 8.62 | 5.45
NOR 545.0 NORTHAM TOWNSITE | Rural Short | Shire of Northam | 1394 | 247.3 | 202.5 | 4.91 | 2.09
NOR 545.0 NORTHAM TOWNSITE | Rural Short | Shire of York | 48 | 779.5 | 202.5 | 15.47 | 2.09
NOR 545.0 NORTHAM TOWNSITE | Rural Short | Total | 1442 | 265.2 | 202.5 | 5.26 | 2.09
NP 303.0 RICHMOND ST | Urban | Total - City of Vincent | 909 | 87.7 | 123.8 | 0.23 | 1.25
NP 305.0 159 LOFTUS ST | Urban | City of Vincent | 3172 | 138.3 | 123.8 | 1.3 | 1.25
NP 305.0 159 LOFTUS ST | Urban | City of Stirling | 1197 | 143.4 | 123.8 | 1.35 | 1.25
NP 305.0 159 LOFTUS ST | Urban | Total | 4369 | 139.7 | 123.8 | 1.32 | 1.25
NP 307.0 CHARLES ST SOUTH | Urban | Town of Cambridge | 1215 | 295.6 | 123.8 | 2.25 | 1.25
NP 307.0 CHARLES ST SOUTH | Urban | City of Vincent | 1190 | 313.8 | 123.8 | 2.38 | 1.25
NP 307.0 CHARLES ST SOUTH | Urban | City of Stirling | 443 | 109.9 | 123.8 | 0.84 | 1.25
NP 307.0 CHARLES ST SOUTH | Urban | Total | 2848 | 275.6 | 123.8 | 2.09 | 1.25
NP 309.0 VIEW ST | Urban | City of Vincent | 2044 | 262.2 | 123.8 | 4.98 | 1.25
NP 309.0 VIEW ST | Urban | City of Stirling | 553 | 128.6 | 123.8 | 2.44 | 1.25
NP 309.0 VIEW ST | Urban | Total | 2619 | 234.2 | 123.8 | 4.44 | 1.25
NP 310.0 110 LOFTUS ST | Urban | City of Vincent | 311 | 132.8 | 123.8 | 0.38 | 1.25
NP 310.0 110 LOFTUS ST | Urban | Town of Cambridge | 35 | 0 | 123.8 | 0 | 1.25
NP 310.0 110 LOFTUS ST | Urban | Total | 351 | 117.1 | 123.8 | 0.34 | 1.25
NP 316.0 215 LOFTUS ST | Urban | City of Vincent | 1296 | 150.8 | 123.8 | 2.61 | 1.25
NP 316.0 215 LOFTUS ST | Urban | City of Stirling | 280 | 92 | 123.8 | 1.59 | 1.25
NP 316.0 215 LOFTUS ST | Urban | Total | 1576 | 140.4 | 123.8 | 2.43 | 1.25
NP 317.0 PALMERSTON ST | Urban | City of Vincent | 533 | 0 | 123.8 | 0 | 1.25
NP 317.0 PALMERSTON ST | Urban | City of Perth | 398 | 0 | 123.8 | 0 | 1.25
NP 317.0 PALMERSTON ST | Urban | Total | 931 | 0 | 123.8 | 0 | 1.25
NP 319.0 BOURKE ST WEST | Urban | City of Vincent | 997 | 121.8 | 123.8 | 2.5 | 1.25
NP 319.0 BOURKE ST WEST | Urban | Town of Cambridge | 838 | 44.7 | 123.8 | 0.92 | 1.25
NP 319.0 BOURKE ST WEST | Urban | Total | 1835 | 86.3 | 123.8 | 1.77 | 1.25
NP 321.0 CHARLES ST NORTH | Urban | Total - City of Vincent | 1352 | 7.9 | 123.8 | 0.08 | 1.25
NP 323.0 CHARLES ST FLATS | Urban | City of Vincent | 1107 | 79.3 | 123.8 | 0.91 | 1.25
NP 323.0 CHARLES ST FLATS | Urban | City of Perth | 90 | 210.8 | 123.8 | 2.41 | 1.25
NP 323.0 CHARLES ST FLATS | Urban | Total | 1197 | 81.7 | 123.8 | 0.93 | 1.25
NP 324.0 WOODVILLE ST | Urban | City of Vincent | 1636 | 60 | 123.8 | 0.22 | 1.25
NP 324.0 WOODVILLE ST | Urban | City of Stirling | 415 | 0.5 | 123.8 | 0 | 1.25
NP 324.0 WOODVILLE ST | Urban | Total | 2051 | 47.8 | 123.8 | 0.18 | 1.25
OC 501.0 ANTILL L/S | Urban | Total - City of Melville | 1949 | 110.1 | 123.8 | 0.78 | 1.25
OC 504.0 LUCAS ST | Urban | Total - City of Melville | 742 | 458.5 | 123.8 | 2.88 | 1.25
OC 505.0 WEATHERBURN WAY | Urban | City of Cockburn | 1989 | 350.8 | 123.8 | 5.79 | 1.25
OC 505.0 WEATHERBURN WAY | Urban | City of Melville | 1948 | 108.6 | 123.8 | 1.79 | 1.25
OC 505.0 WEATHERBURN WAY | Urban | Total | 3937 | 219.1 | 123.8 | 3.61 | 1.25
OC 508.0 BOWEN ST | Urban | City of Fremantle | 1066 | 236.8 | 123.8 | 3.06 | 1.25
OC 508.0 BOWEN ST | Urban | City of Cockburn | 994 | 89.5 | 123.8 | 1.16 | 1.25
OC 508.0 BOWEN ST | Urban | City of Melville | 962 | 159 | 123.8 | 2.05 | 1.25
OC 508.0 BOWEN ST | Urban | Total | 3022 | 156.2 | 123.8 | 2.02 | 1.25
OC 510.0 GARLING ST WEST | Urban | City of Melville | 166 | 0.2 | 123.8 | 0 | 1.25
OC 510.0 GARLING ST WEST | Urban | City of Fremantle | 160 | 1.7 | 123.8 | 0.01 | 1.25
OC 510.0 GARLING ST WEST | Urban | Total | 326 | 0.8 | 123.8 | 0 | 1.25
OC 511.0 240 LEACH HWY | Urban | Total - City of Melville | 1528 | 305.9 | 123.8 | 3.17 | 1.25
OC 516.0 97 GARLING ST | Urban | Total - City of Fremantle | 1640 | 65.6 | 123.8 | 1.22 | 1.25
OC 517.0 GARLING EAST | Urban | Total - City of Melville | 3167 | 1.4 | 123.8 | 0 | 1.25
OP 301.0 401 SCARBOROUGH BEACH RD | Urban | Total - City of Stirling | 462 | 203.8 | 123.8 | 0.58 | 1.25
OP 302.0 L57 SELBY ST NTH | Urban | Total - City of Stirling | 99 | 0 | 123.8 | 0 | 1.25
OP 305.0 433 SCARBOROUGH BEACH RD | Urban | Total - City of Stirling | 809 | 0.2 | 123.8 | 0 | 1.25
OP 310.0 9 KING EDWARD RD | Urban | Total - City of Stirling | 214 | 79.3 | 123.8 | 0.3 | 1.25
OP 311.0 SELBY ST | Urban | Total - City of Stirling | 129 | 0 | 123.8 | 0 | 1.25
OP 323.0 388 SCARBOROUGH | Urban | Total - City of Stirling | 1354 | 23 | 123.8 | 0.08 | 1.25
OP 324.0 HASLER RD/401 SCARBOROUGH | Urban | Total - City of Stirling | 2924 | 181.1 | 123.8 | 2.86 | 1.25
OP 325.0 16 FROBISHER ST | Urban | Total - City of Stirling | 127 | 38.1 | 123.8 | 0.7 | 1.25
OP 327.0 L165 WALTERS DR | Urban | Total - City of Stirling | 62 | 0 | 123.8 | 0 | 1.25
OP 331.0 GUTHRIE ST | Urban | Total - City of Stirling | 605 | 176.9 | 123.8 | 3.01 | 1.25
OP 340.0 4 ELLEN STIRLING/ HOWE ST | Urban | Total - City of Stirling | 1783 | 151.1 | 123.8 | 1.09 | 1.25
OP 341.0 SARICH CT/ 466 SCARBOROUGH | Urban | Total - City of Stirling | 1273 | 34 | 123.8 | 0.19 | 1.25
PBY 504.0 ENDEAVOUR RD | Urban | Total - City of Joondalup | 1962 | 119.9 | 123.8 | 1.18 | 1.25
PBY 507.0 83 GIBSON AVE | Urban | Total - City of Joondalup | 2581 | 181.1 | 123.8 | 2 | 1.25
PBY 508.0 56 WARBURTON AVE | Urban | Total - City of Joondalup | 2467 | 287.2 | 123.8 | 1.44 | 1.25
PBY 516.0 MARMION AVE NORTH | Urban | Total - City of Joondalup | 2746 | 78.1 | 123.8 | 0.24 | 1.25
PBY 526.0 MARMION AVE SOUTH | Urban | Total - City of Joondalup | 3278 | 44.9 | 123.8 | 0.36 | 1.25
PBY 536.0 GIBSON AVE | Urban | Total - City of Joondalup | 2765 | 59.5 | 123.8 | 1.12 | 1.25
PBY 537.0 WHITFORDS AVE EAST | Urban | Total - City of Joondalup | 2500 | 27.9 | 123.8 | 0.1 | 1.25
PBY 540.0 243 GIBSON AVE | Urban | Total - City of Joondalup | 4790 | 163 | 123.8 | 0.89 | 1.25
PCY 302.0 ARTHUR ST | Urban | Total - City of Kalgoorlie-Boulder | 450 | 130.5 | 123.8 | 1.05 | 1.25
PCY 305.0 PICCADILLY NORTH/EGAN | Urban | Total - City of Kalgoorlie-Boulder | 1241 | 263.3 | 123.8 | 2.18 | 1.25
PCY 306.0 PARSON ST | Urban | Total - City of Kalgoorlie-Boulder | 1784 | 233 | 123.8 | 2.24 | 1.25
PCY 309.0 WITTENOOM ST/BROOKMAN ST | Urban | Total - City of Kalgoorlie-Boulder | 1075 | 373.7 | 123.8 | 3.31 | 1.25
PCY 310.0 LIONEL WEST | Rural Short | Total - City of Kalgoorlie-Boulder | 1366 | 353.8 | 202.5 | 3.09 | 2.09
PCY 312.0 LIONEL EAST/PORTER ST | Urban | Total - City of Kalgoorlie-Boulder | 1743 | 676.5 | 123.8 | 6.22 | 1.25
PCY 313.0 LANE ST | Urban | Total - City of Kalgoorlie-Boulder | 353 | 542.9 | 123.8 | 3.88 | 1.25
PCY 323.0 PICCADILLY SOUTH | Urban | Total - City of Kalgoorlie-Boulder | 524 | 297.7 | 123.8 | 2.84 | 1.25
PCY 324.0 KEENAN ST | Urban | Total - City of Kalgoorlie-Boulder | 848 | 280.3 | 123.8 | 3.2 | 1.25
PCY 326.0 EGAN ST | Urban | Total - City of Kalgoorlie-Boulder | 835 | 228.5 | 123.8 | 2.06 | 1.25
PCY 327.0 PORTER ST | Urban | Total - City of Kalgoorlie-Boulder | 1060 | 513.2 | 123.8 | 4.26 | 1.25
PCY 331.0 BROOKMAN ST | Urban | Total - City of Kalgoorlie-Boulder | 1226 | 455.4 | 123.8 | 2.95 | 1.25
PIC 504.0 BRUNSWICK | Rural Short | City of Bunbury | 1232 | 219.8 | 202.5 | 1.95 | 2.09
PIC 504.0 BRUNSWICK | Rural Short | Shire of Dardanup | 434 | 993.3 | 202.5 | 8.79 | 2.09
PIC 504.0 BRUNSWICK | Rural Short | Shire of Harvey | 384 | 628 | 202.5 | 5.56 | 2.09
PIC 504.0 BRUNSWICK | Rural Short | Total | 2051 | 619.1 | 202.5 | 5.48 | 2.09
PIC 505.0 LAPORTE 2 | Rural Short | Shire of Dardanup | 1997 | 276.5 | 202.5 | 4.91 | 2.09
PIC 505.0 LAPORTE 2 | Rural Short | Shire of Harvey | 1581 | 183.7 | 202.5 | 3.26 | 2.09
PIC 505.0 LAPORTE 2 | Rural Short | Total | 3591 | 238.2 | 202.5 | 4.23 | 2.09
PIC 510.0 LAPORTE 1 | Urban | Total - Shire of Dardanup | 2580 | 128.5 | 123.8 | 1.49 | 1.25
PIC 511.0 C.S.B.P. | Rural Short | Shire of Capel | 481 | 812.9 | 202.5 | 4.61 | 2.09
PIC 511.0 C.S.B.P. | Rural Short | City of Bunbury | 151 | 1032.5 | 202.5 | 5.85 | 2.09
PIC 511.0 C.S.B.P. | Rural Short | Total | 642 | 865.3 | 202.5 | 4.9 | 2.09
PIC 513.0 MOORE RD | Rural Short | Total - Shire of Dardanup | 310 | 957.7 | 202.5 | 2.54 | 2.09
PIC 514.0 KIRUP | Rural Long | Shire of Donnybrook-Balingup | 1058 | 1308.2 | 290.5 | 5.63 | 5.45
PIC 514.0 KIRUP | Rural Long | Shire of Dardanup | 838 | 1674.7 | 290.5 | 7.21 | 5.45
PIC 514.0 KIRUP | Rural Long | Shire of Capel | 289 | 1336.1 | 290.5 | 5.75 | 5.45
PIC 514.0 KIRUP | Rural Long | Total | 2202 | 1457.7 | 290.5 | 6.27 | 5.45
PNJ 505.0 PATERSON RD B RMU | Rural Short | Total - Shire of Murray | 185 | 185.1 | 202.5 | 4.96 | 2.09
PNJ 516.0 MURRAY RIVER | Rural Short | Total - Shire of Murray | 2662 | 293.4 | 202.5 | 2.86 | 2.09
PNJ 517.0 L2 OLD MANDURAH RD 3 RMU | Rural Long | Total - Shire of Murray | 4920 | 407.7 | 290.5 | 3 | 5.45
PNJ 527.0 72 OLD MANDURAH RD 3 RMU | Rural Short | Total - Shire of Murray | 122 | 0 | 202.5 | 0 | 2.09
RAN 307.0 75 CHAPMAN RD | Urban | Total - City of Greater Geraldton | 2160 | 12.6 | 123.8 | 0.1 | 1.25
RAN 308.0 L3 NORTH WEST COASTAL HWY | Urban | Total - City of Greater Geraldton | 2460 | 144.6 | 123.8 | 1.33 | 1.25
RAN 321.0 7 SCOTT RD | Rural Short | Total - City of Greater Geraldton | 599 | 2.2 | 202.5 | 0 | 2.09
RAN 323.0 233 DURLACHER ST | Urban | Total - City of Greater Geraldton | 247 | 2547.4 | 123.8 | 12.76 | 1.25
RAN 324.0 53 GERALDTON PRIM/PASS ST | Urban | Total - City of Greater Geraldton | 1725 | 64.7 | 123.8 | 0.61 | 1.25
RAN 341.0 9 HOWES ST | Rural Short | Total - City of Greater Geraldton | 1642 | 165.2 | 202.5 | 1.27 | 2.09
RAN 342.0 19 CARSON ST | Rural Short | Total - City of Greater Geraldton | 736 | 994.3 | 202.5 | 2.76 | 2.09
RAN 351.0 26 CHAPMAN RD | Rural Short | Total - City of Greater Geraldton | 232 | 0 | 202.5 | 0 | 2.09
RAN 352.0 233 DURLACHER ST | Urban | Total - City of Greater Geraldton | 1565 | 34.1 | 123.8 | 0.18 | 1.25
RGN 506.0 WANERIE | Rural Long | Total - Shire of Gingin | 791 | 957 | 290.5 | 7.83 | 5.45
RGN 508.0 BEERMULLAH | Rural Short | Total - Shire of Gingin | 137 | 328.8 | 202.5 | 4.23 | 2.09
RGN 604.0 LANCELIN | Rural Long | Total - Shire of Gingin | 2038 | 798.6 | 290.5 | 10.68 | 5.45
RGN 610.0 MOGUMBER | Rural Long | Shire of Chittering | 141 | 7491.1 | 290.5 | 22.57 | 5.45
RGN 610.0 MOGUMBER | Rural Long | Shire of Victoria Plains | 117 | 4769.8 | 290.5 | 14.37 | 5.45
RGN 610.0 MOGUMBER | Rural Long | Shire of Gingin | 95 | 5346.1 | 290.5 | 16.11 | 5.45
RGN 610.0 MOGUMBER | Rural Long | Shire of Dandaragan | 37 | 7081.1 | 290.5 | 21.34 | 5.45
RGN 610.0 MOGUMBER | Rural Long | Total | 390 | 6118.2 | 290.5 | 18.44 | 5.45
RO 503.0 ANDROMEDA | Urban | Total - City of Rockingham | 4283 | 60.4 | 123.8 | 0.14 | 1.25
RO 504.0 45 LAKE ST | Urban | Total - City of Rockingham | 275 | 66.6 | 123.8 | 0.5 | 1.25
RO 507.0 L1483 FARRIS ST | Urban | Total - City of Rockingham | 856 | 230.1 | 123.8 | 2.41 | 1.25
RO 509.0 BROUGHTON | Urban | Total - City of Rockingham | 2899 | 135.3 | 123.8 | 1.33 | 1.25
RO 510.0 SWINSTONE | Urban | Total - City of Rockingham | 1826 | 13.7 | 123.8 | 0.6 | 1.25
RO 515.0 GREGSON | Urban | Total - City of Rockingham | 1789 | 190.8 | 123.8 | 1.22 | 1.25
RO 519.0 RAY | Urban | City of Rockingham | 1019 | 244 | 123.8 | 2.77 | 1.25
RO 519.0 RAY | Urban | City of Kwinana | 584 | 130.3 | 123.8 | 1.48 | 1.25
RO 519.0 RAY | Urban | Total | 1603 | 203.2 | 123.8 | 2.31 | 1.25
RO 521.0 PATTERSON RD | Urban | Total - City of Rockingham | 189 | 1.2 | 123.8 | 0.01 | 1.25
RO 522.0 MCLEAN | Urban | Total - City of Rockingham | 4210 | 45.3 | 123.8 | 0.15 | 1.25
RO 523.0 READ ST | Urban | Total - City of Rockingham | 4227 | 510.2 | 123.8 | 1.79 | 1.25
RTN 502.0 CYPRESS RD | Urban | Total - City of Canning | 2102 | 117 | 123.8 | 0.95 | 1.25
RTN 505.0 ANN WAY | Urban | Total - City of Canning | 4110 | 93.1 | 123.8 | 0.42 | 1.25
RTN 506.0 L2430 LEACH HWY 1 | Urban | Total - City of Melville | 3296 | 100 | 123.8 | 1.11 | 1.25
RTN 508.0 14 CAMM AVE RMU | Urban | City of Melville | 3191 | 183.8 | 123.8 | 2.22 | 1.25
RTN 508.0 14 CAMM AVE RMU | Urban | City of Cockburn | 82 | 138.2 | 123.8 | 1.67 | 1.25
RTN 508.0 14 CAMM AVE RMU | Urban | Total | 3273 | 182.6 | 123.8 | 2.21 | 1.25
RTN 515.0 L2430 LEACH HWY 2 | Urban | Total - City of Canning | 1408 | 435.3 | 123.8 | 0.82 | 1.25
RTN 519.0 L30 PULO RD | Urban | Total - City of Melville | 2646 | 127.4 | 123.8 | 0.24 | 1.25
RTN 521.0 EWING AVE | Urban | City of Canning | 2625 | 289.3 | 123.8 | 4.46 | 1.25
RTN 521.0 EWING AVE | Urban | City of Melville | 535 | 0 | 123.8 | 0 | 1.25
RTN 521.0 EWING AVE | Urban | Total | 3160 | 240.3 | 123.8 | 3.7 | 1.25
RTN 522.0 PINETREE GULLY RD | Urban | City of Canning | 1412 | 339.4 | 123.8 | 1.76 | 1.25
RTN 522.0 PINETREE GULLY RD | Urban | City of Melville | 672 | 423.6 | 123.8 | 2.19 | 1.25
RTN 522.0 PINETREE GULLY RD | Urban | Total | 2084 | 366.6 | 123.8 | 1.9 | 1.25
RVE 502.0 RUTLAND AVE | Urban | Total - Town of Victoria Park | 207 | 0 | 123.8 | 0 | 1.25
RVE 503.0 53 BURSWOOD RD | Urban | Town of Victoria Park | 2286 | 115 | 123.8 | 0.95 | 1.25
RVE 503.0 53 BURSWOOD RD | Urban | City of South Perth | 104 | 6.6 | 123.8 | 0.05 | 1.25
RVE 503.0 53 BURSWOOD RD | Urban | Total | 2390 | 110.3 | 123.8 | 0.92 | 1.25
RVE 507.0 L1001 ROWE AVE | Urban | Total - City of Belmont | 143 | 0 | 123.8 | 0 | 1.25
RVE 511.0 7 STREATLEY RD | Urban | City of Belmont | 3038 | 13.9 | 123.8 | 0.06 | 1.25
RVE 511.0 7 STREATLEY RD | Urban | Town of Victoria Park | 397 | 0 | 123.8 | 0 | 1.25
RVE 511.0 7 STREATLEY RD | Urban | Total | 3435 | 11.7 | 123.8 | 0.05 | 1.25
RVE 518.0 99 GOODWOOD PDE | Urban | Total - Town of Victoria Park | 274 | 0 | 123.8 | 0 | 1.25
RVE 519.0 57 GALLIPOLI ST | Urban | Total - Town of Victoria Park | 3191 | 0.7 | 123.8 | 0.05 | 1.25
RVE 523.0 RUTLAND AVE | Urban | Total - Town of Victoria Park | 2743 | 13.2 | 123.8 | 0.08 | 1.25
RVE 524.0 2 COOKHM RD | Urban | Town of Victoria Park | 3552 | 5.7 | 123.8 | 0.04 | 1.25
RVE 524.0 2 COOKHM RD | Urban | City of Canning | 121 | 7.6 | 123.8 | 0.06 | 1.25
RVE 524.0 2 COOKHM RD | Urban | Total | 3673 | 5.7 | 123.8 | 0.04 | 1.25
RVE 526.0 OPP 8 ROWE AVE | Urban | City of Belmont | 1762 | 212.3 | 123.8 | 2.84 | 1.25
RVE 526.0 OPP 8 ROWE AVE | Urban | Town of Victoria Park | 117 | 168.6 | 123.8 | 2.25 | 1.25
RVE 526.0 OPP 8 ROWE AVE | Urban | Total | 1879 | 209.5 | 123.8 | 2.8 | 1.25
SNR 504.0 L149 HOLMES ST | Urban | Total - City of Gosnells | 2981 | 56 | 123.8 | 2.12 | 1.25
SNR 505.0 61 CHAMBERLAIN ST | Rural Short | City of Cockburn | 1685 | 112.9 | 202.5 | 2.2 | 2.09
SNR 505.0 61 CHAMBERLAIN ST | Rural Short | City of Armadale | 1302 | 101.6 | 202.5 | 1.98 | 2.09
SNR 505.0 61 CHAMBERLAIN ST | Rural Short | Total | 2987 | 107.6 | 202.5 | 2.1 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | City of Armadale | 1523 | 52.7 | 202.5 | 1.1 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | City of Kwinana | 184 | 178.9 | 202.5 | 3.75 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | City of Gosnells | 171 | 329.6 | 202.5 | 6.91 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | City of Cockburn | 148 | 65.3 | 202.5 | 1.37 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | Shire of Serpentine-Jarrahdale | 97 | 132.1 | 202.5 | 2.77 | 2.09
SNR 507.0 L101 TERRIER PL RMU | Rural Short | Total | 2123 | 92.6 | 202.5 | 1.94 | 2.09
SNR 508.0 L111 NICHOLSON RD | Urban | City of Armadale | 1123 | 48.9 | 123.8 | 1.62 | 1.25
SNR 508.0 L111 NICHOLSON RD | Urban | City of Gosnells | 222 | 0 | 123.8 | 0 | 1.25
SNR 508.0 L111 NICHOLSON RD | Urban | Total | 1345 | 43.7 | 123.8 | 1.45 | 1.25
SNR 516.0 61 CHAMBERLAIN ST | Urban | City of Armadale | 4146 | 245.8 | 123.8 | 2.73 | 1.25
SNR 516.0 61 CHAMBERLAIN ST | Urban | City of Gosnells | 540 | 223.5 | 123.8 | 2.48 | 1.25
SNR 516.0 61 CHAMBERLAIN ST | Urban | Total | 4686 | 243.2 | 123.8 | 2.7 | 1.25
SNR 517.0 11 RANFORD RD | Rural Short | City of Gosnells | 738 | 180 | 202.5 | 7.29 | 2.09
SNR 517.0 11 RANFORD RD | Rural Short | City of Armadale | 471 | 10 | 202.5 | 0.4 | 2.09
SNR 517.0 11 RANFORD RD | Rural Short | City of Canning | 104 | 20.8 | 202.5 | 0.84 | 2.09
SNR 517.0 11 RANFORD RD | Rural Short | City of Cockburn | 52 | 73 | 202.5 | 2.96 | 2.09
SNR 517.0 11 RANFORD RD | Rural Short | Total | 1364 | 66.5 | 202.5 | 2.69 | 2.09
SNR 526.0 MARGARET ST | Urban | Total - City of Armadale | 3963 | 217.3 | 123.8 | 2.98 | 1.25
SNR 527.0 OPP L201 ALLEN RD RMU 1 | Urban | Total - City of Armadale | 2987 | 410.2 | 123.8 | 10.31 | 1.25
SNR 537.0 L545 SOUTHERN RIVER RD | Urban | City of Gosnells | 2496 | 0 | 123.8 | 0 | 1.25
SNR 537.0 L545 SOUTHERN RIVER RD | Urban | City of Armadale | 349 | 0 | 123.8 | 0 | 1.25
SNR 537.0 L545 SOUTHERN RIVER RD | Urban | Total | 2845 | 0 | 123.8 | 0 | 1.25
SNR 539.0 L8008 RANFORD RD | Rural Short | Total - City of Armadale | 3451 | 85.1 | 202.5 | 1.08 | 2.09
SNR 540.0 | Urban | City of Armadale | 3034 | 43.4 | 123.8 | 0.06 | 1.25
SNR 540.0 | Urban | City of Gosnells | 69 | 0 | 123.8 | 0 | 1.25
SNR 540.0 | Urban | Total | 3103 | 42.6 | 123.8 | 0.06 | 1.25
SPK 332.0 1 BAY RD | Rural Short | Town of Claremont | 711 | 0.1 | 202.5 | 0 | 2.09
SPK 332.0 1 BAY RD | Rural Short | City of Nedlands | 405 | 1.1 | 202.5 | 0 | 2.09
SPK 332.0 1 BAY RD | Rural Short | Total | 1116 | 0.5 | 202.5 | 0 | 2.09
SPK 334.0 L11671 STUBBS TCE | Urban | Total - City of Nedlands | 11 | 18.4 | 123.8 | 0.09 | 1.25
SPK 337.0 OPP 4 THE BOULEVARD | Urban | City of Stirling | 560 | 22.4 | 123.8 | 0.18 | 1.25
SPK 337.0 OPP 4 THE BOULEVARD | Urban | Town of Cambridge | 559 | 0 | 123.8 | 0 | 1.25
SPK 337.0 OPP 4 THE BOULEVARD | Urban | Total | 1119 | 11.2 | 123.8 | 0.09 | 1.25
SPK 338.0 21 CUNNINGHAM TCE | Urban | Total - City of Subiaco | 1042 | 19 | 123.8 | 0.07 | 1.25
SPK 345.0 | Urban | City of Subiaco | 549 | 0 | 123.8 | 0 | 1.25
SPK 345.0 | Urban | Town of Cambridge | 157 | 0 | 123.8 | 0 | 1.25
SPK 345.0 | Urban | City of Nedlands | 37 | 9.9 | 123.8 | 0.03 | 1.25
SPK 345.0 | Urban | Total | 743 | 0.5 | 123.8 | 0 | 1.25
SPK 348.0 10 SELBY ST | Urban | Town of Cambridge | 1489 | 100.9 | 123.8 | 0.07 | 1.25
SPK 348.0 10 SELBY ST | Urban | City of Stirling | 781 | 0.9 | 123.8 | 0 | 1.25
SPK 348.0 10 SELBY ST | Urban | City of Subiaco | 73 | 0 | 123.8 | 0 | 1.25
SPK 348.0 10 SELBY ST | Urban | Total | 2344 | 64.8 | 123.8 | 0.04 | 1.25
SPK 349.0 SELBY ST | Urban | Town of Cambridge | 830 | 0 | 123.8 | 0 | 1.25
SPK 349.0 SELBY ST | Urban | City of Subiaco | 532 | 0 | 123.8 | 0 | 1.25
SPK 349.0 SELBY ST | Urban | City of Stirling | 292 | 0 | 123.8 | 0 | 1.25
SPK 349.0 SELBY ST | Urban | Total | 1659 | 10.9 | 123.8 | 0.03 | 1.25
SPK 350.0 20 MELVILLE ST | Urban | City of Nedlands | 1121 | 3.2 | 123.8 | 0.04 | 1.25
SPK 350.0 20 MELVILLE ST | Urban | Town of Claremont | 283 | 0.6 | 123.8 | 0.01 | 1.25
SPK 350.0 20 MELVILLE ST | Urban | Total | 1404 | 2.7 | 123.8 | 0.03 | 1.25
SPK 362.0 40 ALFRED RD | Urban | City of Nedlands | 1113 | 30.2 | 123.8 | 0.16 | 1.25
SPK 362.0 40 ALFRED RD | Urban | Town of Claremont | 699 | 0 | 123.8 | 0 | 1.25
SPK 362.0 40 ALFRED RD | Urban | Total | 1812 | 18.6 | 123.8 | 0.1 | 1.25
SPK 364.0 KEMH RMU 1 | Urban | Town of Cambridge | 308 | 0 | 123.8 | 0 | 1.25
SPK 364.0 KEMH RMU 1 | Urban | City of Subiaco | 262 | 0 | 123.8 | 0 | 1.25
SPK 364.0 KEMH RMU 1 | Urban | Total | 570 | 0 | 123.8 | 0 | 1.25
SPK 366.0 179 SELBY ST | Urban | Town of Cambridge | 637 | 0 | 123.8 | 0 | 1.25
SPK 366.0 179 SELBY ST | Urban | City of Nedlands | 370 | 0 | 123.8 | 0 | 1.25
SPK 366.0 179 SELBY ST | Urban | Total | 1007 | 0 | 123.8 | 0 | 1.25
SPK 378.0 11 JOHN XX111 AVE | Urban | City of Nedlands | 712 | 12.3 | 123.8 | 0.04 | 1.25
SPK 378.0 11 JOHN XX111 AVE | Urban | Town of Cambridge | 413 | 0 | 123.8 | 0 | 1.25
SPK 378.0 11 JOHN XX111 AVE | Urban | Total | 1125 | 7.7 | 123.8 | 0.02 | 1.25
SPK 379.0 339 ONSLOW | Urban | City of Subiaco | 1171 | 0.2 | 123.8 | 0 | 1.25
SPK 379.0 339 ONSLOW | Urban | City of Nedlands | 251 | 79.5 | 123.8 | 0.7 | 1.25
SPK 379.0 339 ONSLOW | Urban | Total | 1424 | 14.2 | 123.8 | 0.13 | 1.25
SVY 507.0 CHDLOW (LS) | Rural Short | Shire of Mundaring | 1323 | 208.1 | 202.5 | 3.12 | 2.09
SVY 507.0 CHDLOW (LS) | Rural Short | City of Swan | 497 | 286.4 | 202.5 | 4.3 | 2.09
SVY 507.0 CHDLOW (LS) | Rural Short | Total | 1820 | 229.4 | 202.5 | 3.44 | 2.09
SVY 516.0 CHIDLOW L/S | Rural Short | Total - Shire of Mundaring | 47 | 86.8 | 202.5 | 1.9 | 2.09
SVY 517.0 MUNDARING L/S | Rural Short | Shire of Mundaring | 1615 | 311.3 | 202.5 | 4.41 | 2.09
SVY 517.0 MUNDARING L/S | Rural Short | City of Swan | 488 | 418.4 | 202.5 | 5.93 | 2.09
SVY 517.0 MUNDARING L/S | Rural Short | Total | 2103 | 336.2 | 202.5 | 4.77 | 2.09
SVY 526.0 1 MUNDARING WEIR 1 | Rural Short | Shire of Mundaring | 23 | 1897.6 | 202.5 | 0.52 | 2.09
SVY 526.0 1 MUNDARING WEIR 1 | Rural Short | City of Kalamunda | 2 | 0 | 202.5 | 0 | 2.09
SVY 526.0 1 MUNDARING WEIR 1 | Rural Short | Total | 25 | 1745.8 | 202.5 | 0.48 | 2.09
SVY 527.0 GREAT EASTERN HWY | Rural Short | Shire of Mundaring | 1184 | 382.2 | 202.5 | 3.39 | 2.09
SVY 527.0 GREAT EASTERN HWY | Rural Short | City of Swan | 30 | 97.3 | 202.5 | 0.86 | 2.09
SVY 527.0 GREAT EASTERN HWY | Rural Short | Total | 1214 | 375 | 202.5 | 3.33 | 2.09
SX 602.0 MOORINE ROCK | Rural Long | Total - Shire of Yilgarn | 223 | 1621.2 | 290.5 | 7.6 | 5.45
SX 608.0 GHOOLI | Rural Short | Total - Shire of Yilgarn | 41 | 1038.4 | 202.5 | 4.29 | 2.09
SX 609.0 BULLFINCH | Rural Long | Shire of Yilgarn | 67 | 201.2 | 290.5 | 3 | 5.45
SX 609.0 BULLFINCH | Rural Long | Shire of Westonia | 49 | 277.2 | 290.5 | 4.13 | 5.45
SX 609.0 BULLFINCH | Rural Long | Shire of Mukinbudin | 8 | 397.8 | 290.5 | 5.93 | 5.45
SX 609.0 BULLFINCH | Rural Long | Shire of Nungarin | 8 | 234.5 | 290.5 | 3.49 | 5.45
SX 609.0 BULLFINCH | Rural Long | Total | 132 | 243 | 290.5 | 3.62 | 5.45
TS 602.0 ENEABBA | Rural Long | Shire of Carnamah | 143 | 1489.5 | 290.5 | 10.76 | 5.45
TS 602.0 ENEABBA | Rural Long | Shire of Three Springs | 104 | 3402.4 | 290.5 | 24.57 | 5.45
TS 602.0 ENEABBA | Rural Long | Total | 251 | 2293 | 290.5 | 16.56 | 5.45
TS 604.0 CARNAMAH | Rural Long | Shire of Carnamah | 338 | 141.5 | 290.5 | 1.05 | 5.45
TS 604.0 CARNAMAH | Rural Long | Shire of Coorow | 241 | 298.5 | 290.5 | 2.21 | 5.45
TS 604.0 CARNAMAH | Rural Long | Shire of Perenjori | 36 | 1131.1 | 290.5 | 8.36 | 5.45
TS 604.0 CARNAMAH | Rural Long | Total | 627 | 259.8 | 290.5 | 1.92 | 5.45
TS 610.0 LATHAM | Rural Long | Shire of Perenjori | 97 | 1329.8 | 290.5 | 5.48 | 5.45
TS 610.0 LATHAM | Rural Long | Shire of Carnamah | 33 | 2022.3 | 290.5 | 8.33 | 5.45
TS 610.0 LATHAM | Rural Long | Shire of Three Springs | 31 | 601.5 | 290.5 | 2.48 | 5.45
TS 610.0 LATHAM | Rural Long | Total | 163 | 1329.3 | 290.5 | 5.48 | 5.45
TS 611.0 MORAWA | Rural Long | Shire of Morawa | 586 | 716.6 | 290.5 | 3.79 | 5.45
TS 611.0 MORAWA | Rural Long | Shire of Perenjori | 252 | 2547.3 | 290.5 | 13.48 | 5.45
TS 611.0 MORAWA | Rural Long | City of Greater Geraldton | 28 | 1482.3 | 290.5 | 7.84 | 5.45
TS 611.0 MORAWA | Rural Long | Shire of Three Springs | 24 | 160.7 | 290.5 | 0.85 | 5.45
TS 611.0 MORAWA | Rural Long | Total | 895 | 1232.1 | 290.5 | 6.52 | 5.45
TS 613.0 MINGENEW | Rural Long | Shire of Mingenew | 388 | 5.6 | 290.5 | 0.04 | 5.45
TS 613.0 MINGENEW | Rural Long | Shire of Three Springs | 79 | 4.6 | 290.5 | 0.04 | 5.45
TS 613.0 MINGENEW | Rural Long | Total | 483 | 5.4 | 290.5 | 0.04 | 5.45
TS 614.0 THREE SPRINGS | Rural Short | Total - Shire of Three Springs | 295 | 497.2 | 202.5 | 2.37 | 2.09
W 306.0 30 BEAUFORT ST | Urban | Total - City of Perth | 23 | 0 | 123.8 | 0 | 1.25
W 311.0 202 PIER ST | Urban | Total - City of Perth | 24 | 0 | 123.8 | 0 | 1.25
W 312.0 34 STIRLING ST | Urban | City of Vincent | 167 | 0 | 123.8 | 0 | 1.25
W 312.0 34 STIRLING ST | Urban | City of Perth | 40 | 0 | 123.8 | 0 | 1.25
W 312.0 34 STIRLING ST | Urban | Total | 207 | 0 | 123.8 | 0 | 1.25
W 318.0 GREGSON ST | Urban | City of Vincent | 856 | 0 | 123.8 | 0 | 1.25
W 318.0 GREGSON ST | Urban | City of Perth | 183 | 0 | 123.8 | 0 | 1.25
W 318.0 GREGSON ST | Urban | Total | 1039 | 0 | 123.8 | 0 | 1.25
WAG 507.0 RADIO 6WA | Rural Long | Shire of West Arthur | 516 | 1188.9 | 290.5 | 5.58 | 5.45
WAG 507.0 RADIO 6WA | Rural Long | Shire of Wagin | 105 | 282.6 | 290.5 | 1.33 | 5.45
WAG 507.0 RADIO 6WA | Rural Long | Shire of Williams | 41 | 1023.9 | 290.5 | 4.81 | 5.45
WAG 507.0 RADIO 6WA | Rural Long | Total | 668 | 1035.5 | 290.5 | 4.86 | 5.45
WAG 510.0 DUMBLYUNG | Rural Long | Shire of Dumbleyung | 436 | 422.8 | 290.5 | 2.91 | 5.45
WAG 510.0 DUMBLYUNG | Rural Long | Shire of Wagin | 208 | 448.4 | 290.5 | 3.09 | 5.45
WAG 510.0 DUMBLYUNG | Rural Long | Shire of Woodanilling | 40 | 934 | 290.5 | 6.43 | 5.45
WAG 510.0 DUMBLYUNG | Rural Long | Total | 697 | 459.9 | 290.5 | 3.17 | 5.45
WAG 512.0 WAGIN | Rural Short | Total - Shire of Wagin | 836 | 180.8 | 202.5 | 1.96 | 2.09
WAI 504.0 73 MALIBU RD | Urban | Total - City of Rockingham | 1563 | 70.2 | 123.8 | 0.62 | 1.25
WAI 505.0 95 THE AVENUE | Urban | Total - City of Rockingham | 3678 | 93.2 | 123.8 | 1.18 | 1.25
WAI 507.0 CURRIE ST | Urban | Total - City of Rockingham | 2980 | 32.9 | 123.8 | 0.61 | 1.25
WAI 516.0 WARNBRO SOUND AVE | Urban | Total - City of Rockingham | 3722 | 10.9 | 123.8 | 0.05 | 1.25
WAI 526.0 CURRIE ST | Urban | Total - City of Rockingham | 4645 | 106.7 | 123.8 | 1.35 | 1.25
WAI 527.0 L461 ENNIS AVE | Urban | Total - City of Rockingham | 3790 | 131.6 | 123.8 | 1.21 | 1.25
WAI 536.0 WARNBRO SOUND AVE SOUTH | Urban | Total - City of Rockingham | 1611 | 258.4 | 123.8 | 1.52 | 1.25
WAI 539.0 L9050 SAFETY BAY RD (LS) | Rural Short | Total - City of Rockingham | 2524 | 15.6 | 202.5 | 0.93 | 2.09
WAI 540.0 190 MANDURAH RD | Rural Short | Total - City of Rockingham | 3757 | 83.5 | 202.5 | 2.08 | 2.09
WD 301.0 35 TILTON TCE | Urban | Total - Town of Cambridge | 886 | 0 | 123.8 | 0 | 1.25
WD 302.0 L3000 UNIVERSITY AVE | Rural Short | City of Stirling | 660 | 5.2 | 202.5 | 0.04 | 2.09
WD 302.0 L3000 UNIVERSITY AVE | Rural Short | Town of Cambridge | 350 | 0 | 202.5 | 0 | 2.09
WD 302.0 L3000 UNIVERSITY AVE | Rural Short | Total | 1010 | 3.4 | 202.5 | 0.02 | 2.09
WD 303.0 30 BUXTON/2 MALTON | Urban | City of Stirling | 2107 | 74.9 | 123.8 | 0.17 | 1.25
WD 303.0 30 BUXTON/2 MALTON | Urban | Town of Cambridge | 879 | 100.6 | 123.8 | 0.23 | 1.25
WD 303.0 30 BUXTON/2 MALTON | Urban | Total | 2986 | 82.6 | 123.8 | 0.19 | 1.25
WD 306.0 42 UNWIN/WEAPONESS SOUTH | Rural Short | City of Stirling | 598 | 0 | 202.5 | 0 | 2.09
WD 306.0 42 UNWIN/WEAPONESS SOUTH | Rural Short | Town of Cambridge | 177 | 0 | 202.5 | 0 | 2.09
WD 306.0 42 UNWIN/WEAPONESS SOUTH | Rural Short | Total | 775 | 0 | 202.5 | 0 | 2.09
WD 336.0 2 EDNAH ST | Urban | Total - City of Stirling | 1302 | 21.1 | 123.8 | 0.07 | 1.25
WD 337.0 73 KALINDA DR | Rural Short | Town of Cambridge | 1000 | 24.2 | 202.5 | 0.04 | 2.09
WD 337.0 73 KALINDA DR | Rural Short | City of Nedlands | 217 | 270.3 | 202.5 | 0.48 | 2.09
WD 337.0 73 KALINDA DR | Rural Short | Town of Claremont | 143 | 144.1 | 202.5 | 0.26 | 2.09
WD 337.0 73 KALINDA DR | Rural Short | Total | 1360 | 73.8 | 202.5 | 0.13 | 2.09
WD 339.0 20 LUITA ST | Urban | Total - City of Stirling | 1485 | 9.1 | 123.8 | 0.07 | 1.25
WD 340.0 28 NORMAN ST/ULSTER RD | Urban | Town of Cambridge | 702 | 51.9 | 123.8 | 0.16 | 1.25
WD 340.0 28 NORMAN ST/ULSTER RD | Urban | City of Stirling | 189 | 12.9 | 123.8 | 0.04 | 1.25
WD 340.0 28 NORMAN ST/ULSTER RD | Urban | Total | 891 | 43.6 | 123.8 | 0.14 | 1.25
WE 504.0 CANNINGTON | Urban | City of Gosnells | 2612 | 91.1 | 123.8 | 0.69 | 1.25
WE 504.0 CANNINGTON | Urban | City of Canning | 1945 | 251.8 | 123.8 | 1.92 | 1.25
WE 504.0 CANNINGTON | Urban | Total | 4557 | 159.7 | 123.8 | 1.21 | 1.25
WE 505.0 MURRAY RD STH | Urban | City of Kalamunda | 1123 | 13.5 | 123.8 | 0.93 | 1.25
WE 505.0 MURRAY RD STH | Urban | City of Canning | 104 | 43.2 | 123.8 | 2.96 | 1.25
WE 505.0 MURRAY RD STH | Urban | City of Gosnells | 46 | 2.1 | 123.8 | 0.14 | 1.25
WE 505.0 MURRAY RD STH | Urban | Total | 1273 | 15.6 | 123.8 | 1.07 | 1.25
WE 508.0 L1 KURNALL RD | Urban | Total - City of Canning | 177 | 40.4 | 123.8 | 1.05 | 1.25
WE 510.0 35 REDCLIFFE ST | Urban | City of Canning | 2268 | 309.1 | 123.8 | 2.22 | 1.25
WE 510.0 35 REDCLIFFE ST | Urban | City of Gosnells | 497 | 232.2 | 123.8 | 1.67 | 1.25
WE 510.0 35 REDCLIFFE ST | Urban | Total | 2765 | 295.5 | 123.8 | 2.12 | 1.25
WE 511.0 L110 PILBARA RD | Urban | Total - City of Canning | 576 | 216.7 | 123.8 | 1.28 | 1.25
WE 514.0 FURNACE RD | Urban | Total - City of Canning | 85 | 53.9 | 123.8 | 0.22 | 1.25
WE 519.0 1 FELSPAR RD | Urban | Total - City of Kalamunda | 3531 | 95.9 | 123.8 | 1.85 | 1.25
WE 523.0 L15 WELSHPOOL RD | Urban | City of Gosnells | 1131 | 391.8 | 123.8 | 1.73 | 1.25
WE 523.0 L15 WELSHPOOL RD | Urban | City of Canning | 287 | 0 | 123.8 | 0 | 1.25
WE 523.0 L15 WELSHPOOL RD | Urban | Total | 1418 | 311.7 | 123.8 | 1.38 | 1.25
WE 524.0 QUEENS PARK | Urban | Total - City of Canning | 2640 | 138.8 | 123.8 | 1.21 | 1.25
WE 525.0 KEWDALE RD WEST | Urban | City of Canning | 211 | 9.9 | 123.8 | 0.14 | 1.25
WE 525.0 KEWDALE RD WEST | Urban | City of Belmont | 6 | 0 | 123.8 | 0 | 1.25
WE 525.0 KEWDALE RD WEST | Urban | Total | 217 | 9.6 | 123.8 | 0.13 | 1.25
WGA 504.0 8 CHALLENGE BVD | Urban | Total - City of Wanneroo | 1157 | 88 | 123.8 | 1.07 | 1.25
WGA 505.0 1 AMBITION GATE RMU | Rural Short | Total - City of Wanneroo | 2707 | 23.6 | 202.5 | 0.18 | 2.09
WGA 507.0 1 27 BERRIMAN DR | Urban | Total - City of Wanneroo | 335 | 194.1 | 123.8 | 1.59 | 1.25
WGA 508.0 12 FORTITUDE BVD RMU | Urban | Total - City of Wanneroo | 2191 | 0.1 | 123.8 | 0 | 1.25
WGP 508.0 WAROONA | Urban | Shire of Waroona | 1004 | 269 | 123.8 | 3.35 | 1.25
WGP 508.0 WAROONA | Urban | Shire of Murray | 984 | 559.3 | 123.8 | 6.96 | 1.25
WGP 508.0 WAROONA | Urban | Total | 2029 | 378.4 | 123.8 | 4.71 | 1.25
WGP 512.0 HARVEY | Urban | Total - Shire of Harvey | 1370 | 889 | 123.8 | 5.26 | 1.25
WGP 515.0 DRAKESBROOK | Rural Short | Total - Shire of Waroona | 1520 | 74.1 | 202.5 | 1.31 | 2.09
WKT 322.0 WEST KALGOORLIE RD(NORTH) | Urban | Total - City of Kalgoorlie-Boulder | 39 | 175.8 | 123.8 | 2 | 1.25
WKT 323.0 CRAIG RD | Urban | Total - City of Kalgoorlie-Boulder | 1620 | 1028.2 | 123.8 | 5.25 | 1.25
WKT 324.0 WEST KALGOORLIE RD(SOUTH) | Rural Short | Total - City of Kalgoorlie-Boulder | 538 | 202.9 | 202.5 | 2.19 | 2.09
WKT 325.0 L308 BROADWOOD | Rural Short | Total - City of Kalgoorlie-Boulder | 22 | 192 | 202.5 | 2.14 | 2.09
WKT 633.0 GIDJI | Rural Short | Total - City of Kalgoorlie-Boulder | 15 | 1199.3 | 202.5 | 8 | 2.09
WKT 640.0 COOLGARDIE/LYNAS | Rural Short | Total - Shire of Coolgardie | 554 | 705.6 | 202.5 | 7.02 | 2.09
WLN 504.0 L30 MODAL RMU | Urban | Total - City of Canning | 95 | 0 | 123.8 | 0 | 1.25
WLN 505.0 MODAL 3 RMU | Urban | Total - City of Canning | 217 | 43.1 | 123.8 | 0.16 | 1.25
WLN 507.0 TREETOP | Urban | City of Canning | 2033 | 126.4 | 123.8 | 2.26 | 1.25
WLN 507.0 TREETOP | Urban | City of Gosnells | 679 | 109.3 | 123.8 | 1.96 | 1.25
WLN 507.0 TREETOP | Urban | Total | 2712 | 123 | 123.8 | 2.2 | 1.25
WLN 508.0 21 JUBAEA CT | Urban | City of Gosnells | 1849 | 40.1 | 123.8 | 0.64 | 1.25
WLN 508.0 21 JUBAEA CT | Urban | City of Canning | 1367 | 81.1 | 123.8 | 1.29 | 1.25
WLN 508.0 21 JUBAEA CT | Urban | Total | 3216 | 57.8 | 123.8 | 0.92 | 1.25
WMK 305.0 KAMBALDA WEST | Rural Short | Total - Shire of Coolgardie | 413 | 150 | 202.5 | 3.04 | 2.09
WMK 306.0 KAMBALDA EAST | Rural Short | Total - Shire of Coolgardie | 948 | 335.6 | 202.5 | 7.28 | 2.09
WNO 502.0 SHENTON AVE | Urban | Total - City of Wanneroo | 3872 | 117.4 | 123.8 | 4.15 | 1.25
WNO 503.0 BURNS BEACH | Urban | Total - City of Joondalup | 1066 | 20.6 | 123.8 | 0.1 | 1.25
WNO 504.0 L704 YANDELLA PROM | Rural Short | City of Wanneroo | 1731 | 192.8 | 202.5 | 0.95 | 2.09
WNO 504.0 L704 YANDELLA PROM | Rural Short | City of Swan | 79 | 285 | 202.5 | 1.41 | 2.09
WNO 504.0 L704 YANDELLA PROM | Rural Short | Total | 1810 | 196.8 | 202.5 | 0.97 | 2.09
WNO 506.0 L306 WANNEROO RD | Urban | Total - City of Wanneroo | 3145 | 27.4 | 123.8 | 0.14 | 1.25
WNO 510.0 976 WANNEROO RD | Urban | Total - City of Wanneroo | 1970 | 372.7 | 123.8 | 1.71 | 1.25
WNO 514.0 CONNOLLY | Urban | City of Wanneroo | 2631 | 34.9 | 123.8 | 0.16 | 1.25
WNO 514.0 CONNOLLY | Urban | City of Joondalup | 1509 | 9.6 | 123.8 | 0.04 | 1.25
WNO 514.0 CONNOLLY | Urban | Total | 4140 | 25.6 | 123.8 | 0.11 | 1.25
WNO 515.0 WANNEROO S/S RMU | Urban | City of Wanneroo | 149 | 3.4 | 123.8 | 0.02 | 1.25
WNO 515.0 WANNEROO S/S RMU | Urban | City of Joondalup | 4 | 0 | 123.8 | 0 | 1.25
WNO 515.0 WANNEROO S/S RMU | Urban | Total | 153 | 3.3 | 123.8 | 0.02 | 1.25
WNO 519.0 JOONDALUP DR SOUTH | Urban | City of Joondalup | 892 | 0 | 123.8 | 0 | 1.25
WNO 519.0 JOONDALUP DR SOUTH | Urban | City of Wanneroo | 66 | 0 | 123.8 | 0 | 1.25
WNO 519.0 JOONDALUP DR SOUTH | Urban | Total | 958 | 20 | 123.8 | 0.1 | 1.25
WNO 521.0 1387 WANNEROO RD | Rural Short | City of Joondalup | 630 | 0 | 202.5 | 0 | 2.09
WNO 521.0 1387 WANNEROO RD | Rural Short | City of Wanneroo | 17 | 0 | 202.5 | 0 | 2.09
WNO 521.0 1387 WANNEROO RD | Rural Short | Total | 647 | 10.3 | 202.5 | 0.07 | 2.09
WNO 522.0 L9017 WANNEROO RD | Urban | Total - City of Wanneroo | 2241 | 36.5 | 123.8 | 1.04 | 1.25
WNO 524.0 CLARKSON AVE | Rural Short | Total - City of Wanneroo | 1306 | 81.3 | 202.5 | 0.9 | 2.09
WUN 502.0 WUNDOWIE IRON & STEEL | Urban | Total - Shire of Northam | 58 | 487 | 123.8 | 1 | 1.25
WUN 505.0 WOOROLOO GWS PUMPS | Rural Short | Shire of Mundaring | 407 | 191.1 | 202.5 | 0.73 | 2.09
WUN 505.0 WOOROLOO GWS PUMPS | Rural Short | Shire of Northam | 35 | 186.7 | 202.5 | 0.72 | 2.09
WUN 505.0 WOOROLOO GWS PUMPS | Rural Short | Total | 446 | 190.8 | 202.5 | 0.73 | 2.09
WUN 506.0 TIP TOP MEATS | Rural Short | Shire of Northam | 184 | 189.5 | 202.5 | 0.45 | 2.09
WUN 506.0 TIP TOP MEATS | Rural Short | Shire of Mundaring | 87 | 219.5 | 202.5 | 0.52 | 2.09
WUN 506.0 TIP TOP MEATS | Rural Short | Total | 272 | 199 | 202.5 | 0.47 | 2.09
WUN 510.0 BAKERS HILL | Rural Long | Total - Shire of Northam | 1000 | 324.6 | 290.5 | 1.29 | 5.45
WUN 513.0 WUNDOWIE TOWN | Rural Short | Shire of Northam | 495 | 2.7 | 202.5 | 0.01 | 2.09
WUN 513.0 WUNDOWIE TOWN | Rural Short | Shire of Toodyay | 365 | 369.5 | 202.5 | 1.64 | 2.09
WUN 513.0 WUNDOWIE TOWN | Rural Short | Total | 865 | 160.1 | 202.5 | 0.71 | 2.09
Y 308.0 HECTOR EAST/CONSTANCE ST | Urban | Total - City of Stirling | 31 | 0 | 123.8 | 0 | 1.25
Y 309.0 FLINDERS STREET | Urban | Total - City of Stirling | 11 | 0 | 123.8 | 0 | 1.25
Y 310.0 CHARLES ST | Urban | City of Stirling | 9 | 0 | 123.8 | 0 | 1.25
Y 310.0 CHARLES ST | Urban | City of Vincent | 5 | 0 | 123.8 | 0 | 1.25
Y 310.0 CHARLES ST | Urban | Total | 14 | 0 | 123.8 | 0 | 1.25
Y 316.0 HECTOR ST/18 YARRUK ST | Urban | City of Stirling | 2803 | 86.7 | 123.8 | 1.99 | 1.25
Y 316.0 HECTOR ST/18 YARRUK ST | Urban | City of Vincent | 968 | 34.7 | 123.8 | 0.8 | 1.25
Y 316.0 HECTOR ST/18 YARRUK ST | Urban | Total | 3771 | 76 | 123.8 | 1.75 | 1.25
Y 317.0 POWELL ST/LOCKWOOD NORTH | Urban | Total - City of Stirling | 2394 | 114.3 | 123.8 | 0.65 | 1.25
Y 326.0 LOCKWOOD SOUTH/L8 MORGANS S | Urban | Total - City of Stirling | 2801 | 113 | 123.8 | 0.35 | 1.25
Y 327.0 MOULDEN AVE | Urban | Total - City of Stirling | 4015 | 182.5 | 123.8 | 0.67 | 1.25
Y 343.0 402 HECTOR/OPP 83 FLINDERS | Urban | Total - City of Stirling | 2727 | 98.1 | 123.8 | 1.32 | 1.25
Y 344.0 4 BLYTHE AV | Urban | Total - City of Stirling | 1283 | 125.3 | 123.8 | 1.2 | 1.25
Y 345.0 34 BLYTHE AV | Urban | Total - City of Stirling | 2091 | 81.1 | 123.8 | 1.08 | 1.25
Y 347.0 31 CONSTANCE ST | Urban | Total - City of Stirling | 2598 | 69.4 | 123.8 | 0.37 | 1.25
Y 348.0 312 CAPE ST | Urban | Total - City of Stirling | 2651 | 181.1 | 123.8 | 3.12 | 1.25
YLN 605.0 MARVEL LOCH TOWN | Urban | Total - Shire of Yilgarn | 90 | 423.1 | 123.8 | 4.04 | 1.25
YLN 606.0 MARVEL LOCH SOUTH | Rural Short | Total - Shire of Yilgarn | 27 | 4224.9 | 202.5 | 18.48 | 2.09
YLN 609.0 SOUTHERN CROSS TOWN | Urban | Total - Shire of Yilgarn | 448 | 546.8 | 123.8 | 6.02 | 1.25
YLN 613.0 BOONDI | Rural Short | Shire of Yilgarn | 6 | 792.2 | 202.5 | 6.79 | 2.09
YLN 613.0 BOONDI | Rural Short | Shire of Coolgardie | 6 | 610.6 | 202.5 | 5.23 | 2.09
YLN 613.0 BOONDI | Rural Short | Total | 11 | 700.3 | 202.5 | 6 | 2.09
YP 502.0 ROMEO RD A | Urban | Total - City of Wanneroo | 4243 | 20.1 | 123.8 | 0.98 | 1.25
YP 505.0 ROMEO RD C | Rural Short | Total - City of Wanneroo | 4726 | 412.7 | 202.5 | 2.65 | 2.09
YP 507.0 YP507-A RMU | Rural Short | Total - City of Wanneroo | 840 | 164.6 | 202.5 | 2.45 | 2.09
YP 514.0 YP 514-A RMU | Rural Short | Total - City of Wanneroo | 4274 | 719.2 | 202.5 | 8.19 | 2.09
YP 517.0 YP 517-A RMU | Rural Short | Shire of Gingin | 868 | 172.2 | 202.5 | 4.56 | 2.09
YP 517.0 YP 517-A RMU | Rural Short | City of Wanneroo | 451 | 448 | 202.5 | 11.86 | 2.09
YP 517.0 YP 517-A RMU | Rural Short | Total | 1319 | 263.5 | 202.5 | 6.98 | 2.09
YP 530.0 ROMEO RD B | Rural Short | Total - City of Wanneroo | 3588 | 103 | 202.5 | 2 | 2.09

## Appendix B2
LOCAL_GOVERNMENT_AREA | SCNRRR_AREA | CUSTOMERS | SAIDI | SAIDI_SSB | SAIFI | SAIFI_SSB
City of Albany | Rural Short | 17706 | 94.4 | 202.5 | 2.05 | 2.09
City of Albany | Rural Long | 2924 | 604.5 | 290 | 7.45 | 4.45
City of Albany | Total | 20630 | 165.2 | 214.5 | 2.79 | 2.41
City of Armadale | Urban | 28093 | 169.4 | 123.8 | 2.06 | 1.25
City of Armadale | Rural Short | 13489 | 274.6 | 202.5 | 3 | 2.09
City of Armadale | Total | 41582 | 202 | 149.7 | 2.35 | 1.53
Shire of Augusta-Margaret River | Rural Long | 7405 | 186.2 | 290 | 2.63 | 4.45
Shire of Augusta-Margaret River | Rural Short | 3197 | 246.4 | 202.5 | 5.44 | 2.09
Shire of Augusta-Margaret River | Total | 10602 | 201.9 | 263.7 | 3.44 | 3.74
Town of Bassendean | Total - Urban | 8053 | 156.8 | 123.8 | 1.19 | 1.25
City of Bayswater | Urban | 34898 | 126.4 | 123.8 | 0.84 | 1.25
City of Bayswater | Rural Short | 420 | 0 | 202.5 | 0 | 2.09
City of Bayswater | Total | 35318 | 124.4 | 124.7 | 0.83 | 1.26
City of Belmont | Total - Urban | 22090 | 147 | 123.8 | 1.91 | 1.25
Shire of Beverley | Total - Rural Long | 1184 | 1301.9 | 290 | 16.18 | 4.45
Shire of Boddington | Total - Rural Long | 1067 | 378 | 290 | 2.28 | 4.45
Shire of Boyup Brook | Total - Rural Long | 1133 | 202.3 | 290 | 1.12 | 4.45
Shire of Bridgetown-Greenbushes | Total - Rural Long | 3049 | 246.3 | 290 | 3.33 | 4.45
Shire of Brookton | Total - Rural Long | 650 | 1237.4 | 290 | 10.62 | 4.45
Shire of Broomehill-Tambellup | Rural Long | 663 | 268.8 | 290 | 3.01 | 4.45
Shire of Broomehill-Tambellup | Rural Short | 22 | 380.8 | 202.5 | 4.36 | 2.09
Shire of Broomehill-Tambellup | Total | 685 | 267.4 | 287.3 | 3 | 4.38
Shire of Bruce Rock | Total - Rural Long | 687 | 584.8 | 290 | 4.95 | 4.45
City of Bunbury | Urban | 14747 | 741.2 | 123.8 | 1.92 | 1.25
City of Bunbury | Rural Short | 3791 | 147.9 | 202.5 | 2.47 | 2.09
City of Bunbury | Total | 18538 | 615.7 | 139.6 | 2.02 | 1.42
City of Busselton | Rural Short | 20760 | 250.1 | 202.5 | 4.78 | 2.09
City of Busselton | Rural Long | 4141 | 459.3 | 290 | 3.33 | 4.45
City of Busselton | Total | 24901 | 281 | 217.1 | 4.47 | 2.49
Town of Cambridge | Urban | 10599 | 71.8 | 123.8 | 0.51 | 1.25
Town of Cambridge | Rural Short | 1534 | 15.5 | 202.5 | 0.02 | 2.09
Town of Cambridge | Total | 12133 | 64.4 | 133.7 | 0.45 | 1.36
City of Canning | Urban | 39672 | 185.3 | 123.8 | 2.16 | 1.25
City of Canning | Rural Short | 3557 | 119.5 | 202.5 | 2.41 | 2.09
City of Canning | Total | 43229 | 178.6 | 129.8 | 2.17 | 1.31
Shire of Capel | Rural Long | 3089 | 692.3 | 290 | 4.02 | 4.45
Shire of Capel | Urban | 2952 | 337.1 | 123.8 | 2.06 | 1.25
Shire of Capel | Rural Short | 2047 | 265.7 | 202.5 | 4.37 | 2.09
Shire of Capel | Total | 8088 | 450 | 207.5 | 3.36 | 2.69
Shire of Carnamah | Rural Long | 525 | 394.2 | 290 | 2.93 | 4.45
Shire of Carnamah | Rural Short | 12 | 912.9 | 202.5 | 3.67 | 2.09
Shire of Carnamah | Total | 537 | 399.2 | 287.8 | 2.9 | 4.39
Shire of Chapman Valley | Total - Rural Long | 867 | 1586.3 | 290 | 6.16 | 4.45
Shire of Chittering | Rural Long | 2546 | 917.5 | 290 | 5.82 | 4.45
Shire of Chittering | Rural Short | 412 | 398.2 | 202.5 | 2.19 | 2.09
Shire of Chittering | Total | 2958 | 824.3 | 277.7 | 5.19 | 4.12
Town of Claremont | Urban | 4476 | 9.6 | 123.8 | 0.04 | 1.25
Town of Claremont | Rural Short | 844 | 18.1 | 202.5 | 0.05 | 2.09
Town of Claremont | Total | 5320 | 10.9 | 135.7 | 0.05 | 1.38
City of Cockburn | Urban | 37652 | 185.3 | 123.8 | 1.94 | 1.25
City of Cockburn | Rural Short | 18306 | 177.3 | 202.5 | 2.45 | 2.09
City of Cockburn | Total | 55958 | 181.1 | 149.4 | 2.08 | 1.52
Shire of Collie | Rural Short | 3656 | 255.2 | 202.5 | 1.78 | 2.09
Shire of Collie | Rural Long | 1033 | 47.8 | 290 | 1.12 | 4.45
Shire of Collie | Total | 4689 | 207.6 | 221.9 | 1.62 | 2.61
Shire of Coolgardie | Total - Rural Short | 1935 | 404.1 | 202.5 | 6.24 | 2.09
Shire of Coorow | Rural Short | 860 | 466.3 | 202.5 | 3.97 | 2.09
Shire of Coorow | Rural Long | 408 | 1001.1 | 290 | 3.73 | 4.45
Shire of Coorow | Total | 1268 | 630.2 | 230.6 | 3.84 | 2.85
Shire of Corrigin | Total - Rural Long | 815 | 1211.3 | 290 | 7.37 | 4.45
Town of Cottesloe | Total - Urban | 4062 | 7.4 | 123.8 | 0.04 | 1.25
Shire of Cranbrook | Total - Rural Long | 774 | 489.9 | 290 | 4.94 | 4.45
Shire of Cuballing | Total - Rural Long | 510 | 333 | 290 | 1.83 | 4.45
Shire of Cunderdin | Total - Rural Long | 795 | 960.5 | 290 | 7.01 | 4.45
Shire of Dalwallinu | Total - Rural Long | 961 | 3192.8 | 290 | 13.8 | 4.45
Shire of Dandaragan | Total - Rural Long | 3394 | 1219.3 | 290 | 4.85 | 4.45
Shire of Dardanup | Rural Short | 2883 | 498.6 | 202.5 | 4.43 | 2.09
Shire of Dardanup | Urban | 2564 | 155.6 | 123.8 | 1.8 | 1.25
Shire of Dardanup | Rural Long | 885 | 1704.2 | 290 | 6.3 | 4.45
Shire of Dardanup | Total | 6332 | 522.3 | 183.1 | 3.58 | 2.09
Shire of Denmark | Total - Rural Long | 4072 | 534.2 | 290 | 6.95 | 4.45
Shire of Donnybrook-Balingup | Total - Rural Long | 3391 | 715.6 | 290 | 3.49 | 4.45
Shire of Dowerin | Total - Rural Long | 492 | 1051.7 | 290 | 11.37 | 4.45
Shire of Dumbleyung | Total - Rural Long | 525 | 472.1 | 290 | 3.8 | 4.45
Town of East Fremantle | Total - Urban | 3460 | 41.8 | 123.8 | 0.26 | 1.25
City of Fremantle | Total - Urban | 18451 | 84.7 | 123.8 | 0.85 | 1.25
Shire of Gingin | Rural Long | 4006 | 1096.6 | 290 | 9.19 | 4.45
Shire of Gingin | Rural Short | 1021 | 135.2 | 202.5 | 4.02 | 2.09
Shire of Gingin | Total | 5027 | 881.2 | 272 | 7.96 | 3.97
Shire of Gnowangerup | Total - Rural Long | 923 | 983.3 | 290 | 4.94 | 4.45
Shire of Goomalling | Total - Rural Long | 685 | 1569.5 | 290 | 5.49 | 4.45
City of Gosnells | Urban | 48487 | 113.7 | 123.8 | 1.38 | 1.25
City of Gosnells | Rural Short | 3201 | 131 | 202.5 | 2.04 | 2.09
City of Gosnells | Total | 51688 | 114.3 | 128.6 | 1.42 | 1.3
City of Greater Geraldton | Urban | 10418 | 201.4 | 123.8 | 1.01 | 1.25
City of Greater Geraldton | Rural Short | 6856 | 297.8 | 202.5 | 1.06 | 2.09
City of Greater Geraldton | Rural Long | 3172 | 1844 | 290 | 8.89 | 4.45
City of Greater Geraldton | Total | 20446 | 479.8 | 175.2 | 2.21 | 2.01
Shire of Harvey | Rural Short | 10332 | 352.6 | 202.5 | 3.26 | 2.09
Shire of Harvey | Rural Long | 1591 | 703.2 | 290 | 2.21 | 4.45
Shire of Harvey | Urban | 1390 | 593 | 123.8 | 4.35 | 1.25
Shire of Harvey | Total | 13313 | 415.3 | 204 | 3.21 | 2.28
Shire of Irwin | Total - Rural Long | 2493 | 1044.3 | 290 | 14.48 | 4.45
Shire of Jerramungup | Total - Rural Long | 1137 | 2007.1 | 290 | 17.99 | 4.45
City of Joondalup | Urban | 61901 | 101.8 | 123.8 | 0.84 | 1.25
City of Joondalup | Rural Short | 3786 | 87.2 | 202.5 | 0.54 | 2.09
City of Joondalup | Total | 65687 | 100.6 | 128.3 | 0.82 | 1.3
City of Kalamunda | Urban | 12954 | 112.6 | 123.8 | 1.99 | 1.25
City of Kalamunda | Rural Short | 12415 | 103.1 | 202.5 | 1.64 | 2.09
City of Kalamunda | Total | 25369 | 107.5 | 162.2 | 1.81 | 1.66
City of Kalgoorlie-Boulder | Urban | 13034 | 463.3 | 123.8 | 3.55 | 1.25
City of Kalgoorlie-Boulder | Rural Short | 2014 | 321.7 | 202.5 | 2.84 | 2.09
City of Kalgoorlie-Boulder | Total | 15048 | 447.8 | 134.5 | 3.47 | 1.36
Shire of Katanning | Rural Short | 2008 | 14.9 | 202.5 | 0.11 | 2.09
Shire of Katanning | Rural Long | 320 | 112.6 | 290 | 1.7 | 4.45
Shire of Katanning | Total | 2328 | 28.1 | 214.5 | 0.32 | 2.41
Shire of Kellerberrin | Rural Short | 649 | 324.7 | 202.5 | 3.57 | 2.09
Shire of Kellerberrin | Rural Long | 88 | 1480.1 | 290 | 4.04 | 4.45
Shire of Kellerberrin | Total | 737 | 453.8 | 213.2 | 3.57 | 2.38
Shire of Kent | Total - Rural Long | 433 | 621.7 | 290 | 2.47 | 4.45
Shire of Kojonup | Rural Short | 789 | 260.5 | 202.5 | 4.76 | 2.09
Shire of Kojonup | Rural Long | 487 | 468 | 290 | 4.47 | 4.45
Shire of Kojonup | Total | 1276 | 334.9 | 235.7 | 4.58 | 2.99
Shire of Kondinin | Total - Rural Long | 669 | 2181.1 | 290 | 6.78 | 4.45
Shire of Koorda | Total - Rural Long | 373 | 1265.2 | 290 | 13.48 | 4.45
Shire of Kulin | Total - Rural Long | 601 | 1345.3 | 290 | 5.47 | 4.45
City of Kwinana | Rural Short | 14362 | 224.3 | 202.5 | 3.59 | 2.09
City of Kwinana | Urban | 6378 | 174.3 | 123.8 | 2.35 | 1.25
City of Kwinana | Total | 20740 | 206.7 | 178.8 | 3.17 | 1.84
Shire of Lake Grace | Total - Rural Long | 1086 | 1489.8 | 290 | 7.65 | 4.45
City of Mandurah | Urban | 39033 | 141.9 | 123.8 | 2.04 | 1.25
City of Mandurah | Rural Short | 10329 | 332.7 | 202.5 | 2.88 | 2.09
City of Mandurah | Total | 49362 | 180 | 140.4 | 2.2 | 1.43
Shire of Manjimup | Rural Long | 4170 | 508.3 | 290 | 3.39 | 4.45
Shire of Manjimup | Rural Short | 1720 | 267.2 | 202.5 | 1.23 | 2.09
Shire of Manjimup | Total | 5890 | 444 | 264.6 | 2.76 | 3.77
City of Melville | Urban | 43338 | 98.7 | 123.8 | 0.89 | 1.25
City of Melville | Rural Short | 2218 | 1 | 202.5 | 0.01 | 2.09
City of Melville | Total | 45556 | 93.3 | 127.5 | 0.84 | 1.29
Shire of Merredin | Rural Short | 1362 | 467.4 | 202.5 | 4.3 | 2.09
Shire of Merredin | Rural Long | 665 | 526.7 | 290 | 3.22 | 4.45
Shire of Merredin | Total | 2027 | 487.5 | 231.3 | 3.9 | 2.87
Shire of Mingenew | Total - Rural Long | 414 | 1128.6 | 290 | 5.81 | 4.45
Shire of Moora | Rural Short | 954 | 54.3 | 202.5 | 2.08 | 2.09
Shire of Moora | Rural Long | 617 | 2224.8 | 290 | 13.77 | 4.45
Shire of Moora | Total | 1571 | 891.9 | 237.7 | 6.56 | 3.04
Shire of Morawa | Total - Rural Long | 595 | 738.5 | 290 | 5.54 | 4.45
Town of Mosman Park | Total - Urban | 4275 | 58.2 | 123.8 | 0.92 | 1.25
Shire of Mount Marshall | Total - Rural Long | 486 | 2493.9 | 290 | 15.62 | 4.45
Shire of Mukinbudin | Total - Rural Long | 402 | 2994.5 | 290 | 22.31 | 4.45
Shire of Mundaring | Rural Short | 13565 | 356.7 | 202.5 | 3.51 | 2.09
Shire of Mundaring | Urban | 3156 | 107.4 | 123.8 | 1.47 | 1.25
Shire of Mundaring | Total | 16721 | 308.1 | 187.4 | 3.11 | 1.93
Shire of Murray | Rural Long | 4933 | 261.6 | 290 | 2.31 | 4.45
Shire of Murray | Rural Short | 3659 | 417 | 202.5 | 5.81 | 2.09
Shire of Murray | Urban | 1191 | 420 | 123.8 | 4.72 | 1.25
Shire of Murray | Total | 9783 | 333.8 | 235.6 | 3.85 | 3.14
Shire of Nannup | Total - Rural Long | 1129 | 766.7 | 290 | 3.73 | 4.45
Shire of Narembeen | Total - Rural Long | 610 | 1822.3 | 290 | 10.98 | 4.45
Shire of Narrogin | Rural Short | 1668 | 506.5 | 202.5 | 10.26 | 2.09
Shire of Narrogin | Rural Long | 1142 | 311.5 | 290 | 1.47 | 4.45
Shire of Narrogin | Total | 2810 | 423.6 | 238.6 | 6.64 | 3.06
City of Nedlands | Urban | 8929 | 30.4 | 123.8 | 0.16 | 1.25
City of Nedlands | Rural Short | 653 | 92.2 | 202.5 | 0.15 | 2.09
City of Nedlands | Total | 9582 | 34.5 | 129.4 | 0.16 | 1.31
Shire of Northam | Rural Short | 4632 | 193.6 | 202.5 | 3.27 | 2.09
Shire of Northam | Rural Long | 1346 | 324.9 | 290 | 1.86 | 4.45
Shire of Northam | Urban | 89 | 385.1 | 123.8 | 1.21 | 1.25
Shire of Northam | Total | 6068 | 222.7 | 220.4 | 2.89 | 2.59
Shire of Northampton | Total - Rural Long | 2569 | 1304.9 | 290 | 7.36 | 4.45
Shire of Nungarin | Total - Rural Long | 171 | 1225.5 | 290 | 11.11 | 4.45
Shire of Peppermint Grove | Total - Urban | 695 | 95.7 | 123.8 | 0.35 | 1.25
Shire of Perenjori | Total - Rural Long | 384 | 2020 | 290 | 7.41 | 4.45
City of Perth | Urban | 10794 | 43.3 | 123.8 | 0.27 | 1.25
City of Perth | CBD | 5902 | 46.8 | 13.7 | 0.68 | 0.21
City of Perth | Rural Short | 378 | 0.2 | 202.5 | 0.01 | 2.09
City of Perth | Total | 17074 | 43.1 | 86.6 | 0.4 | 0.9
Shire of Pingelly | Total - Rural Long | 747 | 604.9 | 290 | 4.28 | 4.45
Shire of Plantagenet | Rural Long | 2999 | 450.6 | 290 | 4.34 | 4.45
Shire of Plantagenet | Rural Short | 67 | 287.5 | 202.5 | 3.02 | 2.09
Shire of Plantagenet | Total | 3066 | 440 | 288.1 | 4.24 | 4.4
Shire of Quairading | Total - Rural Long | 668 | 3348.8 | 290 | 13.16 | 4.45
Shire of Ravensthorpe | Total - Rural Long | 472 | 1233.7 | 290 | 7.99 | 4.45
City of Rockingham | Urban | 50283 | 130.4 | 123.8 | 1.07 | 1.25
City of Rockingham | Rural Short | 10782 | 128.3 | 202.5 | 2.01 | 2.09
City of Rockingham | Total | 61065 | 129.3 | 138.1 | 1.23 | 1.4
Shire of Serpentine-Jarrahdale | Urban | 6986 | 167.1 | 123.8 | 1.73 | 1.25
Shire of Serpentine-Jarrahdale | Rural Short | 3641 | 530.2 | 202.5 | 5.5 | 2.09
Shire of Serpentine-Jarrahdale | Rural Long | 2770 | 235.2 | 290 | 3.43 | 4.45
Shire of Serpentine-Jarrahdale | Total | 13397 | 276.8 | 179.1 | 3.07 | 2.13
City of South Perth | Total - Urban | 22131 | 57.2 | 123.8 | 0.26 | 1.25
City of Stirling | Urban | 107391 | 126.6 | 123.8 | 1.11 | 1.25
City of Stirling | Rural Short | 2881 | 38.2 | 202.5 | 1.09 | 2.09
City of Stirling | Total | 110272 | 123.7 | 126 | 1.11 | 1.27
City of Subiaco | Total - Urban | 10275 | 9.5 | 123.8 | 0.19 | 1.25
City of Swan | Urban | 41389 | 90 | 123.8 | 1.34 | 1.25
City of Swan | Rural Short | 30536 | 152.2 | 202.5 | 1.82 | 2.09
City of Swan | Total | 71925 | 116.2 | 156.9 | 1.58 | 1.6
Shire of Tammin | Rural Long | 251 | 1382.2 | 290 | 7.96 | 4.45
Shire of Tammin | Rural Short | 14 | 1713.3 | 202.5 | 19.29 | 2.09
Shire of Tammin | Total | 265 | 1368.4 | 285.5 | 8.38 | 4.33
Shire of Three Springs | Rural Short | 302 | 520.7 | 202.5 | 2.52 | 2.09
Shire of Three Springs | Rural Long | 238 | 779.5 | 290 | 5.47 | 4.45
Shire of Three Springs | Total | 540 | 619.4 | 241.8 | 3.73 | 3.15
Shire of Toodyay | Rural Long | 1798 | 680.8 | 290 | 5.64 | 4.45
Shire of Toodyay | Rural Short | 1062 | 318.7 | 202.5 | 2.08 | 2.09
Shire of Toodyay | Total | 2860 | 537.1 | 256.9 | 4.24 | 3.56
Shire of Trayning | Total - Rural Long | 324 | 523.6 | 290 | 6.34 | 4.45
Town of Victoria Park | Urban | 17001 | 57.5 | 123.8 | 0.75 | 1.25
Town of Victoria Park | Rural Short | 1709 | 0.2 | 202.5 | 0 | 2.09
Town of Victoria Park | Total | 18710 | 51.8 | 130.9 | 0.68 | 1.33
Shire of Victoria Plains | Total - Rural Long | 725 | 1910.1 | 290 | 9.15 | 4.45
City of Vincent | Total - Urban | 20543 | 111.4 | 123.8 | 1.3 | 1.25
Shire of Wagin | Rural Short | 845 | 177.7 | 202.5 | 1.93 | 2.09
Shire of Wagin | Rural Long | 356 | 421.2 | 290 | 2.16 | 4.45
Shire of Wagin | Total | 1201 | 247.1 | 228.4 | 1.98 | 2.79
Shire of Wandering | Total - Rural Long | 340 | 364.2 | 290 | 1.98 | 4.45
City of Wanneroo | Urban | 64151 | 68.7 | 123.8 | 0.96 | 1.25
City of Wanneroo | Rural Short | 26953 | 254 | 202.5 | 2.88 | 2.09
City of Wanneroo | Total | 91104 | 121.9 | 147.6 | 1.51 | 1.5
Shire of Waroona | Rural Short | 1496 | 64.4 | 202.5 | 1.28 | 2.09
Shire of Waroona | Urban | 1076 | 398.3 | 123.8 | 5.15 | 1.25
Shire of Waroona | Total | 2572 | 205.6 | 169.3 | 3 | 1.74
Shire of West Arthur | Rural Long | 652 | 1040.1 | 290 | 5.08 | 4.45
Shire of West Arthur | Rural Short | 8 | 91 | 202.5 | 1.5 | 2.09
Shire of West Arthur | Total | 660 | 1012 | 289 | 4.95 | 4.42
Shire of Westonia | Urban | 148 | 771 | 123.8 | 2.81 | 1.25
Shire of Westonia | Rural Long | 79 | 2558.8 | 290 | 14.83 | 4.45
Shire of Westonia | Rural Short | 1 | 61.5 | 202.5 | 2 | 2.09
Shire of Westonia | Total | 228 | 1375.8 | 185.2 | 6.94 | 2.42
Shire of Wickepin | Total - Rural Long | 505 | 1540.6 | 290 | 9.53 | 4.45
Shire of Williams | Total - Rural Long | 663 | 174.3 | 290 | 1.73 | 4.45
Shire of Wongan-Ballidu | Total - Rural Long | 989 | 1923.7 | 290 | 6.3 | 4.45
Shire of Woodanilling | Total - Rural Long | 314 | 339.4 | 290 | 3.84 | 4.45
Shire of Wyalkatchem | Total - Rural Long | 430 | 935.5 | 290 | 12.24 | 4.45
Shire of Yilgarn | Urban | 547 | 528.6 | 123.8 | 5.64 | 1.25
Shire of Yilgarn | Rural Long | 304 | 1745 | 290 | 10.15 | 4.45
Shire of Yilgarn | Rural Short | 75 | 2139.5 | 202.5 | 9.46 | 2.09
Shire of Yilgarn | Total | 926 | 1045.2 | 184.4 | 7.34 | 2.36
Shire of York | Rural Long | 2236 | 502.7 | 290 | 3.94 | 4.45
Shire of York | Rural Short | 57 | 840.5 | 202.5 | 6.99 | 2.09
Shire of York | Total | 2293 | 506.2 | 287.8 | 3.98 | 4.39